## Master XRef
ENTRY # | MP # | DEVICE CODE | EQUIP. CODE | ID CODE | INSTRUMENT TAG # | REFERENCE DRAWING No. | DRAWING ID # | FUNCTIONAL DESCRIPTION | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | CONSTRUCTION NOTES
1 | GF-MP-026 | ESV | FTS | 101 | ESV-FTS-101 | 9517-PID-103 | 11 | Emergency Shutoff Valve | Fisher | N550 w/ P327D | 1.25 | 1.25 | FNPT | Emergency Shutoff Valve w/ Pneumatic Release
2 | GF-MP-017 | FCV | FTS | 101 | FCV-FTS-101 | 9517-PID-103 | 7 | Flow Control Valve (FTS Liquid Line) | Wheatley | 822-023072-131 | 2 | 2 | FNPT | Check Valve - Carbon Steel Body/ SS Clapper
3 | GF-MP-017 | FCV | FTS | 102 | FCV-FTS-102 | 9517-PID-103 | 15 | Flow Control Valve (FTS Vapor Line) | Fisher | 105 | 1.25 | 1.25 | FNPT | Excess Flow Valve
1 | GF-MP-017 | FCV | IAS | 101 | FCV-IAS-101 | 9517-PID-101 | 8 | Flow Control Valve for (FCV-TANK1-101) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
4 | GF-MP-019 | FCV | IAS | 101 | FCV-IAS-101 | 9517-PID-101 | 9 | Flow Control Valve for (FCV-TANK2-101) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
2 | GF-MP-017 | FCV | IAS | 101 | FCV-IAS-101 | 9517-PID-101 | 12 | Flow Control Valve for (FCV-TANK1-102) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
5 | GF-MP-017 | FCV | IAS | 101 | FCV-IAS-101 | 9517-PID-101 | 13 | Flow Control Valve for (FCV-TANK2-102) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
3 | GF-MP-018 | FCV | IAS | 101 | FCV-IAS-101 | 9517-PID-101 | 20 | Flow Control Valve for (FCV-TANK1-103) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
6 | GF-MP-017 | FCV | IAS | 101 | FCV-IAS-101 | 9517-PID-101 | 21 | Flow Control Valve for (FCV-TANK2-103) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
7 | GF-MP-017 | FCV | IAS | 102 | FCV-IAS-102 | 9517-PID-101 | 28 | IAS Solenoid Valve for Tank #1 | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
| GF-MP-053 | FCV | IAS | 102 | FCV-IAS-102 | 9517-PID-101 | 28 | IAS Solenoid Valve for Tank #1 | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT
8 | GF-MP-017 | FCV | IAS | 103 | FCV-IAS-103 | 9517-PID-101 | 29 | IAS Solenoid Valve for Tank #2 | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
| GF-MP-053 | FCV | IAS | 103 | FCV-IAS-103 | 9517-PID-101 | 29 | IAS Solenoid Valve for Tank #2 | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT
| GF-MP-053 | FCV | IAS | 119 | FCV-IAS-103 | 9517-PID-104a | 1 | Instrument Air Main Solenoid Valve | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.5 | 0.5 | FNPT
9 | GF-MP-017 | FCV | IAS | 104 | FCV-IAS-104 | 9517-PID-101 | 32 | IAS Solenoid Valve for (FCV-NG-103) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
10 | GF-MP-017 | FCV | IAS | 105 | FCV-IAS-105 | 9517-PID-101 | 33 | Flow Control Valve for (FCV-NG-103) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT | Flow Control Valve 1/8 "
| GF-MP-017 | FCV | IAS | 106 | FCV-IAS-106 | 12023-PID-102-R03 | 27 | IAS Solenoid Valve for (FCV-VAP-102) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT
| GF-MP-017 | FCV | IAS | 107 | FCV-IAS-107 | 12023-PID-102-R03 | 28 | IAS Flow Control Valve for (FCV-VAP-102) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT
1 | GF-MP-017 | FCV | IAS | 108 | FCV-IAS-108 | 9517-PID-105 | 7 | Control Air Solenoid Valve for (FCV-MIX-121) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
2 | GF-MP-017 | FCV | IAS | 109 | FCV-IAS-109 | 9517-PID-105 | 9 | Control Air Flow Control Valve for (FCV-MIX-101) | Schrader-Bellows | SPF400B | 0.25 | 0.25 | FNPT | Flow Control Valve 1/4" FNPT
3 | GF-MP-017 | FCV | IAS | 110 | FCV-IAS-110 | 9517-PID-105 | 8 | Control Air Solenoid Valve for (FCV-MIX-101) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
4 | GF-MP-017 | FCV | IAS | 111 | FCV-IAS-111 | 9517-PID-105 | 32 | Control Air Solenoid Valve for (FCV-MIX-111) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
5 | GF-MP-017 | FCV | IAS | 112 | FCV-IAS-112 | 9517-PID-105 | 50 | Control Air Flow Control Valve for (FCV-MIX-106) | Schrader-Bellows | SPF400B | 0.25 | 0.25 | FNPT | Flow Control Valve 1/4" FNPT
6 | GF-MP-017 | FCV | IAS | 113 | FCV-IAS-113 | 9517-PID-105 | 49 | Control Air Solenoid Valve for (FCV-MIX-106) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
7 | GF-MP-017 | FCV | IAS | 114 | FCV-IAS-114 | 9517-PID-105 | 56 | Control Air Flow Control Valve for (FCV-MIX-108) | Schrader-Bellows | SPF400B | 0.25 | 0.25 | FNPT | Flow Control Valve 1/4" FNPT
8 | GF-MP-017 | FCV | IAS | 115 | FCV-IAS-115 | 9517-PID-105 | 55 | Control Air Solenoid Valve for (FCV-MIX-108) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
9 | GF-MP-017 | FCV | IAS | 116 | FCV-IAS-116 | 9517-PID-105 | 61 | Control Air Flow Control Valve for (FCV-MIX-104) | Schrader-Bellows | SPF400B | 0.25 | 0.25 | FNPT | Flow Control Valve 1/4" FNPT
10 | GF-MP-017 | FCV | IAS | 117 | FCV-IAS-117 | 9517-PID-105 | 59 | Control Air Solenoid Valve for (FCV-MIX-104) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
11 | GF-MP-017 | FCV | IAS | 118 | FCV-IAS-118 | 9517-PID-105 | 5 | Control Air Solenoid Valve for (FCV-MIX-121) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
1 | GF-MP-017 | FCV | IAS | 119 | FCV-IAS-119 | 9517-PID-104 | 1 | Instrument Air Main Solenoid Valve | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.5 | 0.5 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
12 | GF-MP-017 | FCV | IAS | 120 | FCV-IAS-120 | 9517-PID-105 | 3 | Control Air Solenoid Valve for (FCV-MIX-123) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT | 3-way, SS body, 24 VDC, Class F, 10W
13 | GF-MP-017 | FCV | IAS | 121 | FCV-IAS-121 | 9517-PID-105 | 2 | Control Air Flow Control Valve for (FCV-MIX-123) | Schrader-Bellows | SPF400B | 0.25 | 0.25 | FNPT | Flow Control Valve 1/4" FNPT
| GF-MP-017 | FCV | IAS | 122 | FCV-IAS-122 | 12023-PID-102-R03 | 20 | IAS Solenoid Valve for (FCV-VAP-101) | Parker Skinner | 71315SN2MNJ1N0H111C2 | 0.25 | 0.25 | FNPT
| GF-MP-017 | FCV | IAS | 123 | FCV-IAS-123 | 12023-PID-102-R03 | 21 | IAS Flow Control Valve for (FCV-VAP-101) | Schraeder-Bellows | SPF200B | 0.125 | 0.125 | FNPT
14 | GF-MP-017 | FCV | MIX | 101 | FCV-MIX-101 | 9517-PID-105 | 17 | Blender Propane Vapor Inlet Actuated Ball Valve | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-053 | FCV | MIX | 101 | FCV-MIX-101 | 9517-PID-105a | 17 | Blender Propane Vapor Inlet Actuated Ball Valve | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
15 | GF-MP-017 | FCV | MIX | 102 | FCV-MIX-102 | 9517-PID-105 | 20 | Blender Propane Vapor Pressure Control Valve #2 | Fisher | V150 - V Ball | 2 | 2 | ANSI 150# | V150 W/Type 2052 Size 1 Diaphragm FO Actuator, DVC6200 Positioner, 4200 Position Transmitter
16 | GF-MP-017 | FCV | MIX | 103 | FCV-MIX-103 | 9517-PID-105 | 29 | Propane Vapor Check Valve | Wheatley | 510-025027-121 | 2 | 2 | ANSI 150# | Carbon Steel Flanged End Check Valve, Raised Face
17 | GF-MP-017 | FCV | MIX | 104 | FCV-MIX-104 | 9517-PID-105 | 76 | Process Air Inlet Actuated Ball Valve #1 | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-053 | FCV | MIX | 104 | FCV-MIX-104 | 9517-PID-105b | 76 | Process Air Inlet Actuated Ball Valve #1 | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
18 | GF-MP-017 | FCV | MIX | 106 | FCV-MIX-106 | 9517-PID-105 | 77 | Process Air Inlet Actuated Ball Valve # 2 | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-053 | FCV | MIX | 106 | FCV-MIX-106 | 9517-PID-105c | 77 | Process Air Inlet Actuated Ball Valve # 2 | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
19 | GF-MP-017 | FCV | MIX | 108 | FCV-MIX-108 | 9517-PID-105 | 93 | Blender Air Supply Vent Valve (Double Block - Normally Open) | Jamesbury/Triac | 9FB223600XT/2R200SR--LT | 1 | 1 | FNPT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-053 | FCV | MIX | 108 | FCV-MIX-108 | 9517-PID-105c | 93 | Blender Air Supply Vent Valve (Double Block - Normally Open) | Jamesbury/Triac | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator | 1 | 1 | FNPT | 9FB223600XT/2R200SR--LT
20 | GF-MP-017 | FCV | MIX | 110 | FCV-MIX-110 | 9517-PID-105 | 89 | Process Air Back Check Valve | Wheatley | 510-025027-121 | 2 | 2 | ANSI 150# | Carbon Steel Flanged End Check Valve, Raised Face
21 | GF-MP-017 | FCV | MIX | 111 | FCV-MIX-111 | 9517-PID-105 | 78 | Process Air Pressure Control Valve | Fisher | V150 - V Ball | 1.5 | 1.5 | ANSI 150# | V150 W/Type 2052 Size 1 Diaphragm FO Actuator, DVC6200 Positioner, 4200 Position Transmitter
22 | GF-MP-017 | FCV | MIX | 121 | FCV-MIX-121 | 9517-PID-105 | 45 | Mixed Gas Outlet AuctatedFlow Control Valve | Kuka/Triac | CBA15BGLN/2R300SR--LT | 3 | 3 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-053 | FCV | MIX | 121 | FCV-MIX-121 | 9517-PID-105b | 45 | Mixed Gas Outlet Actuated Flow Control Valve | Kuka/Triac | CBA15BGLN/2R300SR--LT | 3 | 3 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
23 | GF-MP-017 | FCV | MIX | 122 | FCV-MIX-122 | 9517-PID-105 | 38 | Propane Vapor from Tanks Header Check Valve | Wheatley | 822-013072-131 | 1 | 1 | FNPT | CS Body, SS Clapper, 720# Working Pressure
24 | GF-MP-017 | FCV | MIX | 123 | FCV-MIX-123 | 9517-PID-105 | 31 | Propane Vapor from Tanks Vapor Header Ball Valve | Jamesbury | 9FB3600XT | 1 | 1 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
| GF-MP-053 | FCV | MIX | 123 | FCV-MIX-123 | 9517-PID-105a | 31 | Propane Vapor from Tanks Vapor Header Ball Valve | Jamesbury | 9FB3600XT | 1 | 1 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
18 | GF-MP-017 | FCV | NG | 101 | FCV-NG-101 | 9517-PID-101 | 35 | Natural Gas Pad Check Valve #1 | Wheatley | 510-025027-121 | 2 | 2 | ANSI 150# | Carbon Steel Flanged End Check Valve, Raised Face
19 | GF-MP-017 | FCV | NG | 102 | FCV-NG-102 | 9517-PID-101 | 69 | Natural Gas Pad Check Valve #2 | Wheatley | 510-025027-121 | 2 | 2 | ANSI 150# | Carbon Steel Flanged End Check Valve, Raised Face
20 | GF-MP-017 | FCV | NG | 103 | FCV-NG-103 | 9517-PID-101 | 38 | Natural Gas Pad Actuated Ball Valve | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-053 | FCV | NG | 103 | FCV-NG-103 | 9517-PID-101b | 38 | Natural Gas Pad Actuated Ball Valve | Kuka/Triac | CBA15BGLN/2R200SR--LT | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
25 | GF-MP-017 | FCV | QT | 101 | FCV-QT-101 | 9517-PID-105 | 66 | Solenoid Valve Mixed Gas to S.G. Transducer | Parker Skinner | 71216SN2FU00N0H111C2 | 0.25 | 0.25 | FNPT | 2-Way, SS Body, 24VDC, Class F, 10 Watt
36 | GF-MP-017 | FCV | TANK1 | 101 | FCV-TANK1-101 | 9517-PID-101 | 14 | Actuated Internal Valve - Propane Liquid Out Line, Propane Storage Tank No. 1 | Rego | A3213R300 w/ A3213PA | 3 | 3 | MNPT/FNPT | ~300 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
37 | GF-MP-017 | FCV | TANK1 | 102 | FCV-TANK1-102 | 9517-PID-101 | 15 | Actuated Internal Valve - Propane Liquid Fill Line, Propane Storage Tank No. 1 | Rego | A3212R250 w/A3213PA | 2 | 2 | MNPT/FNPT | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
38 | GF-MP-017 | FCV | TANK1 | 103 | FCV-TANK1-103 | 9517-PID-101 | 16 | Actuated Internal Valve - Propane Vapor Line, Propane Storage Tank No. 1 | Rego | A3212R250 w/A3213PA | 2 | 2 | MNPT/FNPT | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
53 | GF-MP-017 | FCV | TANK2 | 101 | FCV-TANK2-101 | 9517-PID-101 | 17 | Actuated Internal Valve - Propane Liquid Out Line, Propane Storage Tank No. 2 | Rego | A3213R300 w/ A3213PA | 3 | 3 | MNPT/FNPT | ~300 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
54 | GF-MP-017 | FCV | TANK2 | 102 | FCV-TANK2-102 | 9517-PID-101 | 18 | Actuated Internal Valve - Propane Liquid Fill Line, Propane Storage Tank No. 2 | Rego | A3212R250 w/A3213PA | 2 | 2 | MNPT/FNPT | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
55 | GF-MP-017 | FCV | TANK2 | 103 | FCV-TANK2-103 | 9517-PID-101 | 51 | Actuated Internal Valve - Propane Vapor Line, Propane Storage Tank No. 2 | Rego | A3212R250 w/A3213PA | 2 | 2 | MNPT/FNPT | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
| GF-MP-017 | FCV | VAP | 101 | FCV-VAP-101 | 12023-PID-102-R03 | 19 | Vaporizer Discharge Actuated Ball Valve | Kuka/Triac | CBA30BGLN/2R300SR--LT | 3 | 3 | ANSI 300#
| GF-MP-053 | FCV | VAP | 101 | FCV-VAP-101 | 12023-PID-102-R03 | 19 | Vaporizer Discharge Actuated Ball Valve | Kuka/Triac | CBA30BGLN/2R300SR--LT | 3 | 3 | ANSI 300# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
| GF-MP-017 | FCV | VAP | 102 | FCV-VAP-102 | 12023-PID-102-R03 | 36 | Vaporizer Discharge Actuated Ball Valve | Kuka/Triac | CBA30BGLN/2R300SR--LT | 3 | 3 | ANSI 300#
69 | GF-MP-017 | FCV | VAP | 102 | FCV-VAP-102 | 9517-PID-101 | 26 | Propane Vapor to Blender Discharge Check Valve | Wheatley | 822-013072-131 | 1 | 1 | FNPT | CS Body, SS Clapper, 720# Working Pressure
| GF-MP-053 | FCV | VAP | 102 | FCV-VAP-102 | 12023-PID-102-R03 | 36 | Vaporizer Discharge Actuated Ball Valve | Kuka/Triac | CBA30BGLN/2R300SR--LT | 3 | 3 | ANSI 300# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
26 | GF-MP-002 | FT | MIX | 101 | FT-MIX-101 | 9517-PID-105 | 21 | Blender Propane Vapor Flow Transmitter | Hoffer | HO2X2-15-CB-1MC3PAX-F1SS-X / CAT1-3/O-7-D-X | 2 | 2 | ANSI 150# | HO Series Turbine Meter w/ Cat3 Microprocessor Transmitter
27 | GF-MP-002 | FT | MIX | 102 | FT-MIX-102 | 9517-PID-105 | 79 | Blender Process Air Supply Flow Transmitter | Hoffer | HO2X2-15-CB-1MC3PAX-F1SS-X / CAT3-2-1-1-DC-X-2/O-x | 2 | 2 | ANSI 150# | HO Series Turbine Meter w/ Cat3 Microprocessor Transmitter
| GF-MP-032 | HV | AIR | 101 | HV AIR 101 | 12023-PID-102-R03 | 10 | Process Air Compressor Discharge Isolation Valve | Kuka | CBA15BGLN | 3 | 3 | ANSI 150#
| GF-MP-032 | HV | AIR | 102 | HV AIR 102 | 12023-PID-102-R03 | 7 | Process Air Tank Drain Valve | RUB | S92EB8 | 1 | 1 | FNPT
| GF-MP-032 | HV | AIR | 103 | HV AIR 103 | 12023-PID-102-R03 | 5 | Process Air Tank Instrument Isolation Valve | Dragon | 10M517G | 0.5 | 0.5 | MXFNPT
| GF-MP-032 | HV | AIR | 104 | HV AIR 104 | 12023-PID-102-R03 | 2 | Process Air Compressor Discharge Isolation Valve | Kuka | CBA15BGLN | 3 | 3 | ANSI 150#
| GF-MP-032 | HV | AIR | 105 | HV AIR 105 | 12023-PID-102-R03 | 1 | Process Air Compressor Discharge Isolation Valve | Kuka | CBA15BGLN | 3 | 3 | ANSI 150#
| GF-MP-032 | HV | IAS | 104 | HV IAS 104 | 12023-PID-102-R03 | 29 | IAS Vented Ball Valve for (FCV-VAP-102) | RUB | S93B41 | 0.25 | 0.25 | FNPT
| GF-MP-032 | HV | IAS | 118 | HV IAS 118 | 12023-PID-102-R03 | 22 | IAS Vented Ball Valve for (FCV-VAP-101) | RUB | S93B41 | 0.25 | 0.25 | FNPT
| GF-MP-032 | HV | VAP | 101 | HV VAP 101 | 12023-PID-102-R03 | 26 | Vaporizer Inlet Isolation Ball Valve | Kuka | CBA30BGLN | 2 | 2 | ANSI 300#
| GF-MP-032 | HV | VAP | 102 | HV VAP 102 | 12023-PID-102-R03 | 16 | Instrument Isolation Ball Valve | Dragon | 10M517G | 0.5 | 0.5 | MNPT x FNPT
| GF-MP-032 | HV | VAP | 103 | HV VAP 103 | 12023-PID-102-R03 | 24 | Vaporizer 1 Inlet Isolation Ball Valve | Titan | YS-62-CS | 2 | 2 | ANSI 300#
| GF-MP-032 | HV | VAP | 104 | HV VAP 104 | 12023-PID-102-R03 | 38 | Vaporizer 2 Inlet Isolation Ball Valve | Kuka | CBA30BGLN | 2 | 2 | ANSI 300#
| GF-MP-032 | HV | VAP | 105 | HV VAP 105 | 12023-PID-102-R03 | 33 | Instrument Isolation Ball Valve | Dragon | 10M517G | 0.5 | 0.5 | MNPT x FNPT
4 | GF-MP-032 | HV | FTS | 101 | HV-FTS-101 | 9517-PID-103 | 2 | Angle Valve (FTS Liquid Line) | Squib-Taylor | AL317P | 2 | 2 | FNPT | 2" Angle Style Globe Valve
5 | GF-MP-032 | HV | FTS | 102 | HV-FTS-102 | 9517-PID-103 | 8 | Strainer Blow Down Valve | Jamesbury | 9FB3600XT | 1 | 1 | FNPT | Fire Safe, Stainless Steel Body, Stainless Steel Trim
6 | GF-MP-032 | HV | FTS | 103 | HV-FTS-103 | 9517-PID-103 | 3 | Isolation Ball Valve (FTS Liquid Line) | Jamesbury | 9FB3600XT | 2 | 2 | FNPT | Fire, Safe, Stainless Steel Body, Stainless Steel Trim
7 | GF-MP-032 | HV | FTS | 104 | HV-FTS-104 | 9517-PID-103 | 10 | Angle Valve (FTS Vapor Line) | Squibb-Taylor | AL313P | 1.25 | 1.25 | FNPT | 1.25" Angle Style Globe Valve
8 | GF-MP-032 | HV | FTS | 105 | HV-FTS-105 | 9517-PID-103 | 12 | Isolation Ball Valve (FTS Vapor Line) | Jamesbury | 9FB3600XT | 2 | 2 | FNPT | Fire Safe, Stainless Steel Body, Stainless Steel Trim
11 | GF-MP-032 | HV | IAS | 101 | HV-IAS-101 | 9517-PID-101 | 10 | Vented Ball Valve for (FCV-TANK1-101) | Apollo | 7K-101-27 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
14 | GF-MP-032 | HV | IAS | 101 | HV-IAS-101 | 9517-PID-101 | 11 | Vented Ball Valve for (FCV-TANK2-101) | Apollo | 7K-101-27 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
15 | GF-MP-032 | HV | IAS | 101 | HV-IAS-101 | 9517-PID-101 | 19 | Vented Ball Valve for (FCV-TANK2-102) | Apollo | 7K-101-27 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
13 | GF-MP-032 | HV | IAS | 101 | HV-IAS-101 | 9517-PID-101 | 24 | Vented Ball Valve for (FCV-TANK1-103) | Apollo | 7K-101-27 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
16 | GF-MP-032 | HV | IAS | 101 | HV-IAS-101 | 9517-PID-101 | 25 | Vented Ball Valve for (FCV-TANK2-103) | Apollo | 7K-101-27 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
12 | GF-MP-032 | HV | IAS | 101 | HV-IAS-101 | 9517-PID-101 | 52 | Vented Ball Valve for (FCV-TANK1-102) | Apollo | 7K-101-27 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
17 | GF-MP-032 | HV | IAS | 102 | HV-IAS-102 | 9517-PID-101 | 64 | Vented Ball Valve for (FCV-NG-103) | RUB | S93B41 | 0.25 | 0.25 | FNPT | 1/4” Brass Ball Valve, Vented
15 | GF-MP-032 | HV | IAS | 105 | HV-IAS-105 | 9517-PID-103 | 16 | Pneumatic Isolation for ESV Valve | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4" Brass Ball Valve, Vented
28 | GF-MP-032 | HV | IAS | 108 | HV-IAS-108 | 9517-PID-105 | 6 | Control Air Hand Valve for (FCV-MIX-121) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
29 | GF-MP-032 | HV | IAS | 109 | HV-IAS-109 | 9517-PID-105 | 10 | Control Air Hand Valve for (FCV-MIX-101) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
30 | GF-MP-032 | HV | IAS | 110 | HV-IAS-110 | 9517-PID-105 | 33 | Control Air Hand Valve for (FCV-MIX-111) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
31 | GF-MP-032 | HV | IAS | 111 | HV-IAS-111 | 9517-PID-105 | 51 | Control Air Hand Valve for (FCV-MIX-106) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
32 | GF-MP-032 | HV | IAS | 112 | HV-IAS-112 | 9517-PID-105 | 54 | Control Air Hand Valve for (FCV-MIX-108) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
33 | GF-MP-032 | HV | IAS | 113 | HV-IAS-113 | 9517-PID-105 | 60 | Control Air Hand Valve for (FCV-MIX-104) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
34 | GF-MP-032 | HV | IAS | 114 | HV-IAS-114 | 9517-PID-105 | 4 | Control Air Hand Valve for (FCV-MIX-121) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
2 | GF-MP-032 | HV | IAS | 115 | HV-IAS-115 | 9517-PID-104 | 6 | Instrument Air Compressor Discharge Valve | RUB | S92DB8 | 0.5 | 0.5 | FNPT | Non-Vented 1/2" Brass Ball Valve
3 | GF-MP-032 | HV | IAS | 116 | HV-IAS-116 | 9517-PID-104 | 7 | Instrument Air Isolation Ball Valve | RUB | S92DB8 | 0.5 | 0.5 | FNPT | Non-Vented 1/2" Brass Ball Valve
35 | GF-MP-032 | HV | IAS | 117 | HV-IAS-117 | 9517-PID-105 | 1 | Control Air Hand Valve for (FCV-MIX-123) | Rub | S93B41 | 0.25 | 0.25 | FNPT | 1/4", Vented, Brass Ball Valve
36 | GF-MP-032 | HV | MIX | 101 | HV-MIX-101 | 9517-PID-105 | 12 | Blender Propane Supply Blowdown Valve | Jamesbury | 9FB3600XT | 0.5 | 0.5 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
37 | GF-MP-032 | HV | MIX | 102 | HV-MIX-102 | 9517-PID-105 | 85 | Insturment Hand Valve for PT & PI-MIX-103 | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | CS Body, Grafoil Packing - 6000 psig Max
38 | GF-MP-032 | HV | MIX | 103 | HV-MIX-103 | 9517-PID-105 | 18 | Blender Propane Vapor Insturment Hand Valve for PI-MIX & PT-MIX 102 | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | CS Body, Grafoil Packing - 6000 psig Max
39 | GF-MP-032 | HV | MIX | 105 | HV-MIX-105 | 9517-PID-105 | 26 | Blender Air Supply Insturment Hand Valve for PI-MIX & PT-MIX-105 | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | CS Body, Grafoil Packing - 6000 psig Max
40 | GF-MP-032 | HV | MIX | 106 | HV-MIX-106 | 9517-PID-105 | 92 | Blender Strainer Blowdown Valve Process Air (ST-MIX-102) | Jamesbury | 9FB3600XT | 0.5 | 0.5 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
41 | GF-MP-032 | HV | MIX | 108 | HV-MIX-108 | 9517-PID-105 | 86 | Blender Air Supply Insturment Hand Valve for PT & PI-MIX-104 | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | CS Body, Grafoil Packing - 6000 psig Max
42 | GF-MP-032 | HV | MIX | 109 | HV-MIX-109 | 9517-PID-105 | 65 | Blender Air Supply Blowdown Valve | Jamesbury | 9FB3600XT | 0.5 | 0.5 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
43 | GF-MP-032 | HV | MIX | 110 | HV-MIX-110 | 9517-PID-105 | 44 | Mixer Instrument Hand Valve for PT & PI-MIX-106 | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | CS Body, Grafoil Packing - 6000 psig Max
44 | GF-MP-032 | HV | MIX | 111 | HV-MIX-111 | 9517-PID-105 | 57 | Hand Valve (Mixed Gas to Densitometer) | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | Carbon Steel Body, SS Trim, Fire Safe
45 | GF-MP-032 | HV | MIX | 112 | HV-MIX-112 | 9517-PID-105 | 47 | Blender Instrument Hand Valve for PT -MIX-107 | Dragon | 10M517G | 0.5 | 0.5 | MNPT/FNPT | CS Body, Grafoil Packing - 6000 psig Max
46 | GF-MP-032 | HV | MIX | 119 | HV-MIX-119 | 9517-PID-105 | 28 | Blowdown valve for (ST MIX 101) | Jamesbury | 9FB3600XT | 0.5 | 0.5 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
21 | GF-MP-032 | HV | NG | 101 | HV-NG-101 | 9517-PID-101 | 36 | Natural Gas Pad Inlet Ball Valve | Kuka | CBA15BGLN | 2 | 2 | ANSI 150# | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim
22 | GF-MP-032 | HV | NG | 102 | HV-NG-102 | 9517-PID-101 | 66 | Natural Gas Pad Gauge Isolation Valve # 1 | Dragon | 10M517G | 0.5 | 0.5 | MNPT x FNPT | CS Body, Grafoil Packing - 6000 psig Max
23 | GF-MP-032 | HV | NG | 103 | HV-NG-103 | 9517-PID-101 | 67 | Natural Gas Pad Gauge Isolation Valve # 2 | Dragon | 10M517G | 0.5 | 0.5 | MNPT x FNPT | CS Body, Grafoil Packing - 6000 psig Max
47 | GF-MP-032 | HV | QT | 101 | HV-QT-101 | 9517-PID-105 | 62 | Hand Valve Test Port for Air Supply to S.G. Transducer | Jamesbury | 9FB3600XT | 0.25 | 0.25 | FNPT | Stainless Steel Body, SS Trim, Fire Safe
27 | GF-MP-032 | HV | TA | 105 | HV-TA-105 | 9517-PID-101 | 68 | Propane Vapor Line 3-Way Ball Valve for Hydrostatic Relief Valves | Apollo | 76-603 | 0.5 | 0.5 | FNPT | 3-Way, SS Body, and Trim
28 | GF-MP-032 | HV | TA | 106 | HV-TA-106 | 9517-PID-101 | 56 | Propane Vapor Line 3-Way Ball Valve for Hydrostatic Relief Valves | Apollo | 76-603 | 0.5 | 0.5 | FNPT | 3-Way, SS Body, and Trim
29 | GF-MP-032 | HV | TA | 107 | HV-TA-107 | 9517-PID-101 | 23 | Propane Liquid Line 3-Way Ball Valve for Hydrostatic Relief Valves | Apollo | 76-603 | 0.5 | 0.5 | FNPT | 3-Way, SS Body, and Trim
39 | GF-MP-032 | HV | TANK1 | 101 | HV-TANK1-101 | 9517-PID-101 | 61 | Isolation Ball Valve - Liquid Out Line, Propane Storage Tank No. 1 | Kuka | CBA30BG | 3 | 3 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
40 | GF-MP-032 | HV | TANK1 | 102 | HV-TANK1-102 | 9517-PID-101 | 62 | Isolation Ball Valve - Liquid Fill Line Propane, Storage Tank No. 1 | Kuka | CBA30BG | 2 | 2 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
41 | GF-MP-032 | HV | TANK1 | 103 | HV-TANK1-103 | 9517-PID-101 | 58 | Isolation Ball Valve - Natural Gas Line, Propane Storage Tank No. 1 | Kuka | CBA30BG | 2 | 2 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
42 | GF-MP-032 | HV | TANK1 | 104 | HV-TANK1-104 | 9517-PID-101 | 59 | Isolation Ball Valve - Propane Vapor Line Propane Storage Tank No. 1 | Kuka | CBA30BG | 2 | 2 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
43 | GF-MP-032 | HV | TANK1 | 105 | HV-TANK1-105 | 9517-PID-101 | 41 | Instrument Isolation Valve for LI TANK1 102, Propane Storage Tank No. 1 | Anderson Greenwood | H5VIS22A | 0.25 | 0.25 | MNPT x FNPT | 1/4" SS Angle Needle Valve, w/ T Handle
44 | GF-MP-032 | HV | TANK1 | 106 | HV-TANK1-106 | 9517-PID-101 | 48 | Instrument Isolation Valve for PI & PT TANK1 101, Propane Storage Tank No. 1 | Anderson Greenwood | H5VIS22A | 0.25 | 0.25 | MNPT x FNPT | 1/4" SS Angle Needle Valve, w/ T Handle
56 | GF-MP-032 | HV | TANK2 | 101 | HV-TANK2-101 | 9517-PID-101 | 57 | Isolation Ball Valve - Liquid Out Line, Propane Storage Tank No. 2 | Kuka | CBA30BG | 3 | 3 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
57 | GF-MP-032 | HV | TANK2 | 102 | HV-TANK2-102 | 9517-PID-101 | 63 | Isolation Ball Valve - Liquid Fill Line Propane, Storage Tank No. 2 | Kuka | CBA30BG | 2 | 2 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
58 | GF-MP-032 | HV | TANK2 | 103 | HV-TANK2-103 | 9517-PID-101 | 60 | Isolation Ball Valve - Natural Gas Line, Propane Storage Tank No. 2 | Kuka | CBA30BG | 2 | 2 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
59 | GF-MP-032 | HV | TANK2 | 104 | HV-TANK2-104 | 9517-PID-101 | 30 | Isolation Ball Valve - Propane Vapor Line Propane Storage Tank No. 2 | Kuka | CBA30BG | 2 | 2 | ANSI 300# | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
60 | GF-MP-032 | HV | TANK2 | 105 | HV-TANK2-105 | 9517-PID-101 | 5 | Combo Valve for Propane Storage Tank No. 2 | Marshall Excelsior | MEJ415 | 0.75 | 0.25 | MNPT x FNPT | Combo Valve for 85% Bleed Valve, Pressure Gauge
70 | GF-MP-032 | HV | VAP | 103 | HV-VAP-103 | 9517-PID-101 | 31 | Propane Vapor to Blender Discharge Isolation Ball Valve | Jamesbury | 9FB3600XT | 1 | 1 | FNPT | Stainless Steel Body and Trim, Fire Safe
48 | GF-MP-017 | I/Z | MIX | 101 | I/Z-MIX-101 | 9517-PID-105 | 63 | Current to Position Transmitter for (FCV-MIX-111) | Fisher | DVC 6200 | NA | NA | NA | Current to Position Transmitter for (FCV-MIX-111)
49 | GF-MP-017 | I/Z | MIX | 103 | I/Z-MIX-103 | 9517-PID-105 | 11 | Current to Position Transmitter for (FCV-MIX-102) | Fisher | DVC 6200 | NA | NA | NA | Current to Position Transmitter for (FCV-MIX-102)
45 |  | LI | TANK1 | 101 | LI-TANK1-101 | 9517-PID-101 | 49 | Level Indicator for Propane Storage Tank No. 1 | Taylor | ME3862B / 5331 Adapter | 2.5 | NA | MNPT | 11' Diameter Tank Master LP End Mount, 8" Dial
46 |  | LI | TANK1 | 102 | LI-TANK1-102 | 9517-PID-101 | 43 | 85% Spit Valve to be Installed on (HV-TANK1-105) | Marshall Excelsior | MEJ402S | 0.25 | NA | MNPT | 85% Bleeder to be installed on H5VIS22A
61 |  | LI | TANK2 | 101 | LI-TANK2-101 | 9517-PID-101 | 47 | Level Indicator for Propane Storage Tank No. 2 | Taylor | ME3862B / 5331 Adapter | 2.5 | NA | MNPT | 11' Diameter Tank Master LP End Mount, 8" Dial
62 |  | LI | TANK2 | 102 | LI-TANK2-102 | 9517-PID-101 | 6 | 85% Spit Valve to be Installed on (HV-TANK2-105) | Marshall Excelsior | MEJ402S | 0.25 | NA | MNPT | 85% Bleeder to be installed on MEJ415
47 |  | LT | TANK1 | 101 | LT-TANK1-101 | 9517-PID-101 | 40 | Liquid Level Transmitter for Propane Storage Tank No. 1 | MTS | MRA2B1B11A1U110.00S | 0.75 | NA | MNPT | 110" Order Length, 3/4" MNPT, Calibrated 4" to 108.25", -30 to 150 F
63 |  | LT | TANK2 | 101 | LT-TANK2-101 | 9517-PID-101 | 2 | Liquid Level Transmitter for Propane Storage Tank No. 2 | MTS | MRA2B1B11A1U110.00S | 0.75 | NA | MNPT | 110" Order Length, 3/4" MNPT, Calibrated 4" to 108.25", -30 to 150 F
| GF-MP-032 | PA | VAP | 101 | PA VAP 101 | 12023-PID-102-R03 | 13 | Vaporizer Relief Stack Cap | Anthes Weather Cap | WC 5 | 2 | NA | NA
| GF-MP-033 | PA | VAP | 102 | PA VAP 102 | 12023-PID-102-R03 | 14 | Vaporizer Relief Valve Pipe Away Adapter | Rego | 3135-10 | 1.25 | 2 | NPT
| GF-MP-034 | PA | VAP | 103 | PA VAP 103 | 12023-PID-102-R03 | 30 | Vaporizer Relief Stack Cap | Anthes Weather Cap | WC 5 | 2 | NA | NA
| GF-MP-035 | PA | VAP | 104 | PA VAP 104 | 12023-PID-102-R03 | 31 | Vaporizer Relief Valve Pipe Away Adapter | Rego | 3135-10 | 1.25 | 2 | NPT
4 | GF-MP-049 | PCV | IAS | 101 | PCV-IAS-101 | 9517-PID-104 | 8 | Instrument Air Regulator | Control-Air | 300-BC | 0.25 | 0.25 | NPT | Pressure Regulator, Set 70-80 psig
5 | GF-MP-049 | PCV | IAS | 102 | PCV-IAS-102 | 9517-PID-104 | 10 | Instrument Air Regulator | Control-Air | 300-BC | 0.25 | 0.25 | NPT | Pressure Regulator, Set 30-35 psig
50 | GF-MP-049 | PCV | MIX | 101 | PCV-MIX-101 | 9517-PID-105 | 19 | Blender Propane Vapor Pressure Control Valve #1 | Fisher | 1098-EGR | 2 | 2 | ANSI 150# | Steel Body w/ CL150RF Flanges, 6353 Pilot w/ 3-40 Psig Spring Range,125 Psig Main Spring
51 | GF-MP-049 | PCV | MIX | 103 | PCV-MIX-103 | 9517-PID-105 | 74 | Propane-Air to QT Pressure Control Valve | Swagelok | KPR1DRC412A20000 | 0.5 | 0.5 | FNPT | General-Purpose Diaphragm-Sensing, 0-30 psig Range
52 | GF-MP-049 | PCV | MIX | 109 | PCV-MIX-109 | 9517-PID-105 | 82 | Air Pressure Control Valve | Fisher | 1098-EGR | 2 | 2 | ANSI 150# | Steel Body w/ CL150RF Flanges, 6353 Pilot w/ 35-125 Psig Spring Range, size 30 actuator
24 | GF-MP-049 | PCV | NG | 101 | PCV-NG-101 | 9517-PID-101 | 37 | Natural Gas Pad Pressure Regulator | Fisher | 627 | 1 | 1 | FNPT | Steel body, 1/4" orifice, 70-150 psig Spring Range
53 | GF-MP-049 | PCV | QT | 101 | PCV-QT-101 | 9517-PID-105 | 72 | Pressure Regulator Supply Gas to S.G. Transducer | Fisher | R622-BCF | 0.25 | 0.25 | FNPT | 1/2" NPT, 9" to 13" WC Spring Range
| GF-MP-036 | PE | AIR | 101 | PE AIR 101 | 12023-PID-102-R03 | 11 | Process Air Compressor No. 1 | Atlas Copco | GA110-6.9-60 | NA | 3 | FNPT
| GF-MP-038 | PE | AIR | 102 | PE AIR 102 | 12023-PID-102-R03 | 8 | Process Air Compressor | Sylvin Tank | TBD | 3 | 3 | ANSI 150#
| GF-MP-037 | PE | AIR | 102 | PE AIR 102 | 12023-PID-102-R03 | 3 | Process Air Compressor No. 2 | Atlas Copco | GA110-6.9-60 | NA | 3 | FNPT
|  | PE | VAP | 101 | PE VAP 101 | 12023-PID-102-R03 | 23 | Q1650V Vertical Waterbath Vaporizer 1 | Algas-SDI | Q1650V | 1 | 2 | FNPT
|  | PE | VAP | 102 | PE VAP 102 | 12023-PID-102-R03 | 37 | Q1650V Vertical Waterbath Vaporizer 2 | Algas-SDI | Q1650V | 1 | 2 | FNPT
9 |  | PE | FTS | 101 | PE-FTS-101 | 9517-PID-103 | 6 | FTS Bulkhead | Standby Systems | SSI Drawing | 1.25 | 2 | FNPT | Engineered Breakaway Risers
9 |  | PE | FTS | 101 | PE-FTS-101 | 9517-PID-103 | 14 | FTS Bulkhead | Standby Systems | SSI Drawing | 1.25 | 2 | FNPT | Engineered Breakaway Risers
10 |  | PE | FTS | 102 | PE-FTS-102 | 9517-PID-103 | 1 | Liquid Acme Fill Adapter (FTS Liquid Line) | Fisher | ME503-16, ME441F-1 | 2 | 3.25 | MNPT/ACME | 3-1/4" Acme X 2" NPT Acme Adapter/ Cap & Chain
11 |  | PE | FTS | 104 | PE-FTS-104 | 9517-PID-103 | 9 | Vapor Acme Fill Adapter (FTS Vapor Line) | Fisher | ME233, ME431F-1 | 1.25 | 2.25 | MNPT/ACME | 2-1/4" Acme X 1 1/4" NPT Acme Adapter/ Cap & Chain
6 | GF-MP-004 | PE | IAS | 101 | PE-IAS-101 | 9517-PID-104 | 4 | Instrument Air Compressor | Atlas Copco | GX2-150 | NA | NA | NA | 3 HP, 480 VAC 3 phase, 60HZ, capable of 8.5 SCFM, Tank Mounted w/ disconntect swtich
7 |  | PE | IAS | 102 | PE-IAS-102 | 9517-PID-104 | 5 | IAS Dryer and Filter | Stylair | H12N | 0.25 | 0.25 | FNPT | 10 SCFM Capacity, -40 Deg. Dew Point, Pre and After Filters
54 |  | PE | MIX | 101 | PE-MIX-101 | 9517-PID-105 | 53 | Static Mixer | Custom | 59571 | 4 | 4 | WELD | CS w/ Sch. 40, A106 Gr B Pipe Housing, OAL = 16" end to end
55 |  | PE | MIX | 102 | PE-MIX-102 | 9517-PID-105 | 58 | Inlet Filter for QT | Balston | 91S6 | 0.125 | 0.125 | FNPT | SS Housing, Coalescing Filter Element
56 |  | PE | QT | 101 | PE-QT-101 | 9517-PID-105 | 73 | Specific Gravity Transducer | Yokogawa | GD402G-A-E-E/U & GD40T/EJAF3 | 0.375 | 0.25 | Swagelok | Specific Gravity Transducer Sample Panel
| GF-MP-014 | PI | AIR | 101 | PI AIR 101 | 12023-PID-102-R03 | 4 | Process Air Tank Pressure Indicator | US Gauge | 1981 # 150027DM | 0.5 | 0.5 | MNPT
8 | GF-MP-014 | PI | IAS | 101 | PI-IAS-101 | 9517-PID-104 | 2 | Instrument Air Pressure Indicator | Trerice | D83SS2502LA110 | 0.25 | NA | FNPT | 1/4" LM, 2.5" Dial, SS Case, 0-100 Psig Range
9 | GF-MP-014 | PI | IAS | 102 | PI-IAS-102 | 9517-PID-104 | 9 | Instrument Air Pressure Indicator | Trerice | D83SS2502LA110 | 0.25 | NA | FNPT | 1/4" LM, 2.5" Dial, SS Case, 0-100 Psig Range
57 | GF-MP-014 | PI | MIX | 102 | PI-MIX-102 | 9517-PID-105 | 22 | Blender Propane Vapor Inlet Pressure Indicator #2 | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
58 | GF-MP-014 | PI | MIX | 103 | PI-MIX-103 | 9517-PID-105 | 75 | Blender Air Supply Inlet Pressure Indicator #1 | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
59 | GF-MP-014 | PI | MIX | 104 | PI-MIX-104 | 9517-PID-105 | 80 | Blender Air Supply Inlet Pressure Indicator #2 | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
60 | GF-MP-014 | PI | MIX | 105 | PI-MIX-105 | 9517-PID-105 | 23 | Blender Propane Vapor Inlet Pressure Indicator #1 | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
61 | GF-MP-014 | PI | MIX | 106 | PI-MIX-106 | 9517-PID-105 | 43 | Mixed Gas Pressure Indicator | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
62 | GF-MP-014 | PI | MIX | 107 | PI-MIX-107 | 9517-PID-105 | 71 | Propane-Air to QT Pressure Indicator | Trerice | D83SS2502LA110 | 0.25 | NA | MNPT | 2.5" Dial, 0-100 psig, 1/4" LB Mount
63 | GF-MP-014 | PI | MIX | 108 | PI-MIX-108 | 9517-PID-105 | 46 | Mixed Gas Pressure Indicator #2 | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
25 | GF-MP-014 | PI | NG | 101 | PI-NG-101 | 9517-PID-101 | 34 | Natural Gas Pad Pressure Indicator | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4.5" Dial, 1/2" Lower Mount, 0-200 Psig Range
26 | GF-MP-014 | PI | NG | 102 | PI-NG-102 | 9517-PID-101 | 65 | Natural Gas Pad Pressure Indicator | US Gauge | 1981 # 150027DM | 0.5 | NA | MNPT | 4.5" Dial, 1/2" Lower Mount, 0-200 Psig Range
64 | GF-MP-014 | PI | QT | 101 | PI-QT-101 | 9517-PID-105 | 87 | Pressure Indicator to S.G. Transducer | Trerice | 760B2502LT660 | 0.25 | NA | MNPT | 2.5" Dial, 0-30" WC, 1/4" Lower Mount
48 | GF-MP-014 | PI | TANK1 | 101 | PI-TANK1-101 | 9517-PID-101 | 46 | Pressure Indicator for Propane Storage Tank No. 1 | Trerice | 450SS4502LA140 | 0.25 | NA | MNPT | 4.5" Dial, 1/4" LM Connection, 0-300 Psig Range, SS
64 | GF-MP-014 | PI | TANK2 | 101 | PI-TANK2-101 | 9517-PID-101 | 42 | Pressure Indicator for Propane Storage Tank No. 2 | Trerice | 450SS4502LA140 | 0.25 | NA | MNPT | 4.5" Dial, 1/4" LM Connection, 0-300 Psig Range, SS
| GF-MP-006 | PRV | T1 | 1 | PRV-T1-1 | 9517-PID-101 | 72 | Tank 001 Primary Relief Valve #1
| GF-MP-006 | PRV | T1 | 2 | PRV-T1-2 | 9517-PID-101 | 73 | Tank 001 Primary Relief Valve #2
| GF-MP-006 | PRV | T1 | 3 | PRV-T1-3 | 9517-PID-101 | 74 | Tank 001 Primary Relief Valve #3
| GF-MP-006 | PRV | T1 | 4 | PRV-T1-4 | 9517-PID-101 | 75 | Tank 001 Primary Relief Valve #4
| GF-MP-006 | PRV | T2 | 1 | PRV-T2-1 | 9517-PID-101 | 76 | Tank 002 Primary Relief Valve #1
| GF-MP-006 | PRV | T2 | 2 | PRV-T2-2 | 9517-PID-101 | 77 | Tank 002 Primary Relief Valve #2
| GF-MP-006 | PRV | T2 | 3 | PRV-T2-3 | 9517-PID-101 | 78 | Tank 002 Primary Relief Valve #3
| GF-MP-006 | PRV | T2 | 4 | PRV-T2-4 | 9517-PID-101 | 79 | Tank 002 Primary Relief Valve #4
65 | GF-MP-048 | PSH | MIX | 101 | PSH-MIX-101 | 9517-PID-105 | 41 | Mixed Gas High Pressure Switch | Solon | 6PSX-1-2 | 0.5 | NA | MNPT | Class 1 Div 1 0-300 Scale
10 | GF-MP-005 | PSL | IAS | 101 | PSL-IAS-101 | 9517-PID-104 | 3 | Instrument Air Pressure Switch | Solon | 2PSW-12 | 0.25 | 0.25 | FNPT | 0-100 Psig Range, Enclosure
| GF-MP-006 | PSV | AIR | 101 | PSV AIR 101 | 12023-PID-102-R03 | 6 | Process Air Tank Relief Valve | Kunkle | 6283FEV01 | 1" | 1/2" | MNPT x FNPT
| GF-MP-006 | PSV | VAP | 101 | PSV VAP 101 | 12023-PID-102-R03 | 39 | Vaporizer Inlet Pressure Relief Valve | Algas-SDI | Q1650V | 1 | 2 | FNPT
12 | GF-MP-006 | PSV | FTS | 101 | PSV-FTS-101 | 9517-PID-103 | 4 | Hydrostatic Relief Valve (FTS Liquid Line) | Rego | 3125L | 0.25 | NA | MNPT | 400 Psig Hydrostatic Relief Valve
13 | GF-MP-006 | PSV | FTS | 103 | PSV-FTS-103 | 9517-PID-103 | 13 | Hydrostatic Relief Valve (FTS Vapor Line) | Rego | 3125L | 0.25 | NA | MNPT | 400 Psig Hydrostatic Relief Valve
66 | GF-MP-006 | PSV | MIX | 101 | PSV-MIX-101 | 9517-PID-105 | 70 | QT Inlet Relief Valve | Fisher | H120-60 | 0.5 | 0.5 | MXFNPT | 60 PSIG Set Pressure
30 | GF-MP-006 | PSV | TA | 101 | PSV-TA-101 | 9517-PID-101 | 71 | Natural Gas Hydrostatic Relief Valve # 1 | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
31 | GF-MP-006 | PSV | TA | 102 | PSV-TA-102 | 9517-PID-101 | 70 | Natural Gas Hydrostatic Relief Valve # 2 | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
32 | GF-MP-006 | PSV | TA | 103 | PSV-TA-103 | 9517-PID-101 | 27 | Propane Vapor Line Hydrostatic Relief Valve # 1 | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
33 | GF-MP-006 | PSV | TA | 104 | PSV-TA-104 | 9517-PID-101 | 55 | Propane Vapor Line Hydrostatic Relief Valve # 2 | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
34 | GF-MP-006 | PSV | TA | 105 | PSV-TA-105 | 9517-PID-101 | 54 | Propane Liquid Line Hydrostatic Relief Valve # 1 | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
35 | GF-MP-006 | PSV | TA | 106 | PSV-TA-106 | 9517-PID-101 | 53 | Propane Liquid Line Hydrostatic Relief Valve # 2 | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
71 | GF-MP-006 | PSV | VAP | 101 | PSV-VAP-101 | 9517-PID-101 | 22 | Propane Vapor to Blender Hydrostatic Relief Valve | Rego | 3129U w/ 3129-10 | 0.5 | 0.5 | MNPT | 450 Psig Hydrostatic Relief Valve w 3129-10 Pipe Away
67 | GF-MP-015 | PT | MIX | 102 | PT-MIX-102 | 9517-PID-105 | 15 | Blender Propane Vapor Pressure Transmitter #2 | Wika | E-10 # 50033948 | 0.5 | NA | MNPT | 0-200 Psig Range, Wire End
68 | GF-MP-015 | PT | MIX | 103 | PT-MIX-103 | 9517-PID-105 | 64 | Process Air Inlet Pressure Transmitter #1 | Wika | E-10 # 50033948 | 0.5 | NA | MNPT | 0-200 Psig Range, Wire End
69 | GF-MP-015 | PT | MIX | 104 | PT-MIX-104 | 9517-PID-105 | 68 | Blender Air Supply Inlet Pressure Transmitter #2 | Wika | E-10 # 50033948 | 0.5 | NA | MNPT | 0-200 Psig Range, Wire End
70 | GF-MP-015 | PT | MIX | 105 | PT-MIX-105 | 9517-PID-105 | 16 | Blender Propane Vapor Pressure Transmitter #1 | Wika | E-10 # 50033948 | 0.5 | NA | MNPT | 0-200 Psig Range, Wire End
71 | GF-MP-015 | PT | MIX | 106 | PT-MIX-106 | 9517-PID-105 | 36 | Mixed Gas Pressure Transmitter # 1 | Wika | E-10 # 50033948 | 0.5 | NA | MNPT | 0-200 Psig Range, Wire End
72 | GF-MP-015 | PT | MIX | 107 | PT-MIX-107 | 9517-PID-105 | 42 | Mixed Gas Pressure Transmitter # 2 | Wika | E-10 # 50033948 | 0.5 | NA | MNPT | 0-200 Psig Range, Wire End
49 | GF-MP-015 | PT | TANK1 | 101 | PT-TANK1-101 | 9517-PID-101 | 44 | Pressure Indicating Transmitter for Propane Storage Tank No. 1 | Wika | E-10 # 4365182 | 0.5 | NA | MNPT | 0-300 Psig Scale, Explosion Proof, Wire End
65 | GF-MP-015 | PT | TANK2 | 101 | PT-TANK2-101 | 9517-PID-101 | 45 | Pressure Indicating Transmitter for Propane Storage Tank No.2 | Wika | E-10 # 4365182 | 0.5 | NA | MNPT | 0-300 Psig Scale, Explosion Proof, Wire End
| GF-MP-015 | PT | VAP | 101 | PT-VAP-101 | 12023-PID-102-R03 | 15 | Vaporizer Outlet Pressure Transmitter | Wika | E-10 # 4365182 | 0.5 | NA | FNPT
| GF-MP-015 | PT | VAP | 102 | PT-VAP-102 | 12023-PID-102-R03 | 32 | Vaporizer Outlet Pressure Transmitter | Wika | E-10 # 4365182 | 0.5 | NA | FNPT
?? |  |  | QT | 101 | -QT-101 | 9517-PID-105 | 84 | Not on Device TAG Listing
73 | GF-MP-015 | RTD | MIX | 101 | RTD-MIX-101 | 9517-PID-105 | 14 | Blender Propane Vapor Resistance Temperature Device | Pyromation | R1T185L483-LS4C2.509-SL-8HN71 | 0.5 | NA | MNPT | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
74 | GF-MP-015 | RTD | MIX | 102 | RTD-MIX-102 | 9517-PID-105 | 67 | Air Resistance Temperature Device | Pyromation | R1T185L483-LS4C2.509-SL-8HN71 | 0.5 | NA | MNPT | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
75 | GF-MP-015 | RTD | MIX | 103 | RTD-MIX-103 | 9517-PID-105 | 34 | Mixed Gas Vapor Resistance Temperature Device | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 0.5 | NA | MNPT | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
| GF-MP-015 | RTD | VAP | 101 | RTD-VAP-101 | 12023-PID-102-R03 | 17 | Vaporizer Outlet Resistive Temperature Device | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 0.5 | NA | FNPT
| GF-MP-015 | RTD | VAP | 102 | RTD-VAP-102 | 12023-PID-102-R03 | 34 | Vaporizer Outlet Resistive Temperature Device | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 0.5 | NA | FNPT
| GF-MP-009 | ST | VAP | 101 | ST VAP 101 | 12023-PID-102-R03 | 25 | Vaporizer Inlet Strainer | Titan | YS-62-CS | 2 | 2 | ANSI 300#
14 | GF-MP-009 | ST | FTS | 101 | ST-FTS-101 | 9517-PID-103 | 5 | Strainer for (Liquid Fill Line) | Titan | YS-81 CS | 2 | 2 | FNPT | Carbon Steel Body w/ 40Mesh Screen
76 | GF-MP-009 | ST | MIX | 101 | ST-MIX-101 | 9517-PID-105 | 30 | Blender Propane vapor Inlet Strainer | Titan | YS-61-CS | 2 | 2 | ANSI 150# | Carbon Steel Body, SS 40 Mesh Screen
77 | GF-MP-009 | ST | MIX | 102 | ST-MIX-102 | 9517-PID-105 | 90 | Blender Air Inlet Strainer | Titan | YS-61-CS | 2 | 2 | ANSI 150# | Carbon Steel Body, SS 40 Mesh Screen
78 | GF-MP-014 | TI | MIX | 101 | TI-MIX-101 | 9517-PID-105 | 13 | Blender Propane Vapor Temperature Indicator | Dwyer | BTLR325101 | 0.5 | NA | MNPT | Bimetal Thermometer, 3" Dial, 0/200 Deg. F, 2.5" Stem
79 | GF-MP-014 | TI | MIX | 102 | TI-MIX-102 | 9517-PID-105 | 69 | Blender Air Supply Temperature Indicator | Dwyer | BTLS325101 | 0.5 | NA | MNPT | Bimetal Thermometer, 3" Dial, 0/200 Deg. F, 2.5" Stem
80 | GF-MP-014 | TI | MIX | 103 | TI-MIX-103 | 9517-PID-105 | 35 | Mixed Gas Temperature Indicator | ReoTemp | AA-040-1-F43/S4C0409 | 0.5 | NA | MNPT | Bimetal Thermometer, 3" Dial, 0/200 Deg. F, 2.5" Stem
50 | GF-MP-014 | TI | TANK1 | 101 | TI-TANK1-101 | 9517-PID-101 | 50 | Temperature Indicator for Tank No. 1 | Tel-Tru | GT-300R | 0.5 | NA | MNPT | -40 to 160 Deg F, 6" Stem
66 | GF-MP-014 | TI | TANK2 | 101 | TI-TANK2-101 | 9517-PID-101 | 7 | Temperature Indicator for Tank No. 2 | Tel-Tru | GT-300R | 0.5 | NA | MNPT | -40 to 160 Deg F, 6" Stem
| GF-MP-004 | TT | AIR | 101 | TT AIR 101 | 12023-PID-102-R03 | 12 | Process Air Compressor No. 1 | Atlas Copco | GA110-6.9-60 | NA | 3 | FNPT
| GF-MP-004 | TT | AIR | 102 | TT AIR 102 | 12023-PID-102-R03 | 9 | Process Air Compressor No. 2 | Atlas Copco | GA110-6.9-60 | NA | 3 | FNPT
51 | GF-MP-015 | TT | TANK1 | 101 | TT-TANK1-101 | 9517-PID-101 | 39 | Temperature Transmitter for Tank No. 1 | MTS | Part of LT-T1-101 | NA | NA | NA | Internal Temp Transmitter (see LT-TI-101)
67 | GF-MP-015 | TT | TANK2 | 101 | TT-TANK2-101 | 9517-PID-101 | 1 | Temperature Transmitter for Tank No. 2 | MTS | Part of LT-T2-101 | NA | NA | NA | Internal Temp Transmitter (see LT-TI-101)
81 | GF-MP-005 | TW | MIX | 101 | TW-MIX-101 | 9517-PID-105 | 24 | Blender Propane Vapor Temp. RTD Thermowell | Pyromation | included with RTD (Part of RTD-MIX-101) | 0.5 | 0.5 | MNPT/FNPT | 1/2" Process Connection, 1 7/16" Inserction Length
82 | GF-MP-011 | TW | MIX | 102 | TW-MIX-102 | 9517-PID-105 | 25 | Blender Propane Vapor Temp. Indicator Thermowell | Pyromation | LS4C2.509 (Part of TI-MIX-101) | 0.5 | 0.5 | MNPT/FNPT | 1/2" Process Connection, 1 7/16" Inserction Length
83 | GF-MP-005 | TW | MIX | 103 | TW-MIX-103 | 9517-PID-105 | 83 | Blender Air Supply Temp. RTD Thermowell | Pyromation | included with RTD (Part of RTD-MIX-102) | 0.5 | 0.5 | MNPT/FNPT | 1/2" Process Connection, 1 7/16" Inserction Length
84 | GF-MP-011 | TW | MIX | 104 | TW-MIX-104 | 9517-PID-105 | 81 | Blender Air Supply Temp. Indicator Thermowell | Pyromation | LS4C2.509 (Part of TI-MIX-102) | 0.5 | 0.5 | MNPT/FNPT | 1/2" Process Connection, 2.5" Inserction Length
85 | GF-MP-005 | TW | MIX | 105 | TW-MIX-105 | 9517-PID-105 | 40 | Mixed Gas Vapor Temp. RTD Thermowell | Pyromation | included with RTD (Part of RTD-MIX-103) | 0.5 | 0.5 | MNPT/FNPT | 1/2" Process Connection, 2.5" Inserction Length
86 | GF-MP-011 | TW | MIX | 106 | TW-MIX-106 | 9517-PID-105 | 39 | Mixed Gas Temperature Indicator Thermowell | Pyromation | S4C0409 (Part of TI-MIX-103) | 0.5 | 0.5 | MNPT/FNPT | 1/2" Process Connection, 2 1/2" Inserction Length
52 | GF-MP-005 | TW | TANK1 | 101 | TW-TANK1-101 | 9517-PID-101 | 3 | Themowell Included (LT-TANK1-101) | MTS | Part of LT-T1-101 | 0.75 | 0.75 | MNPT x FNPT | Thermowell (see LT-TI-101)
68 | GF-MP-005 | TW | TANK2 | 101 | TW-TANK2-101 | 9517-PID-101 | 4 | Themowell Included (LT-TANK2-101) | MTS | Part of LT-T2-101 | 0.75 | 0.75 | MNPT x FNPT | Thermowell (see LT-TI-101)
| GF-MP-005 | TW | VAP | 101 | TW-VAP-101 | 12023-PID-102-R03 | 18 | Vaporizer Outlet Thermowell for Temperature Transmitter | Pyromation | Part of RTD- VAP-101 | 0.5 | NA | FNPT
| GF-MP-005 | TW | VAP | 102 | TW-VAP-102 | 12023-PID-102-R03 | 35 | Vaporizer Outlet Thermowell for Temperature Transmitter | Pyromation | Part of RTD- VAP-101 | 0.5 | NA | FNPT
87 | GF-MP-017 | ZSC | MIX | 101 | ZSC-MIX-101 | 9517-PID-105 | 27 | Propane Inlet Valve Proof Closed Switch for (FCV-MIX-101) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Closed Limit Switch (Part of FCV-MIX-101)
88 | GF-MP-017 | ZSC | MIX | 102 | ZSC-MIX-102 | 9517-PID-105 | 88 | Air Inlet Valve # 1 Proof Closed Switch for (FCV-MIX-104) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Closed Limit Switch (Part of FCV-MIX-104)
89 | GF-MP-017 | ZSC | MIX | 103 | ZSC-MIX-103 | 9517-PID-105 | 91 | Air Inlet Valve # 2 Proof Closed Switch for (FCV-MIX-106) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Closed Limit Switch (Part of FCV-MIX-106)
90 | GF-MP-017 | ZSC | MIX | 104 | ZSC-MIX-104 | 9517-PID-105 | 95 | Air Vent Proof Closed Switch for (FCV-MIX-108) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Closed Limit Switch (Part of FCV-MIX-108)
91 | GF-MP-017 | ZSC | MIX | 105 | ZSC-MIX-105 | 9517-PID-105 | 52 | Proof Closed Switch for (FCV-MIX-121) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Closed Limit Switch (Part of FCV-MIX-121)
92 | GF-MP-017 | ZSC | MIX | 106 | ZSC-MIX-106 | 9517-PID-105 | 48 | Tank Vapor Header Proof Closed Switch for (FCV-MIX-123) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Closed Limit Switch (Part of FCV-MIX-108)
93 | GF-MP-017 | ZSO | MIX | 102 | ZSO-MIX-102 | 9517-PID-105 | 94 | Air Vent Valve Explosion Proof Open Switch for (FCV-MIX-108) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Open Limit Switch (Part of FCV-MIX-108)
94 | GF-MP-017 | ZSO | MIX | 103 | ZSO-MIX-103 | 9517-PID-105 | 37 | Proof Open Switch for (FCV-MIX-123) | StoneL | EN33C02RA | 0.5 | NA | NA | Proof Open Limit Switch (Part of FCV-MIX-123)
3-way, SS body, 24 VDC, Class F, 10W
Note on B69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New draft MP
Note on I69: Bill Franki: Corrected "Porpane"
Note on B70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New draft MP
Note on F88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should these all have TAG # HV-IAS-101?
Note on F89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should these all have TAG # HV-IAS-101?
Note on F90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should these all have TAG # HV-IAS-101?
Note on F91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should these all have TAG # HV-IAS-101?
Note on F92: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should these all have TAG # HV-IAS-101?
Note on F93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should these all have TAG # HV-IAS-101?
Note on B136: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B137: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Grouped with Pressure Relief Valves in GF-MP-06
Note on B145: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Grouped with Pressure Relief Valves in GF-MP-06
Note on B146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Grouped with Pressure Relief Valves in GF-MP-06
Note on B147: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Grouped with Pressure Relief Valves in GF-MP-06
Note on I148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Corrected misspelling of "instrument"
Note on B155: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New draft MP
Note on B156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New draft MP
Note on B157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New draft MP
Note on H160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should one of these be PE FTS 103?
Note on H161: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should one of these be PE FTS 103?
Note on B164: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New draft MP
Note on I205: Bill Franki: Corrected misspelling "Reflief"
Note on O205: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Corrected misspelling of "relief"
Note on B236: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-011 due to connection with its TI
Note on B238: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-011 due to connection with its TI
Note on B240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-011 due to connection with its TI
Note on K241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should this be LT-T1-101?
Note on B245: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B246: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B247: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B248: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B249: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B250: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B251: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV
Note on B252: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In MP-017 due to connection with its FCV

## 9517-PID-101
|  |  |  | PROJECT: |  | Berkshire Gas Co. |  |  |  |  | FILE DATE: | 5/4/2012
|  |  |  | JOB NUMBER: |  | 9517 |  |  |  |  | REVISION DATE: | 9/10/2012
|  |  |  | REF. DRAWING: |  | 9517-PID-101 |  |  |  |  | PRINT DATE: | 1/29/2013 10:55
The information contained in this document and/or electronic file(s) is proprietary and/or confidential property Standby Systems, Inc. and shall not be used, reproduced or disclosed to others without the express written consent of the respective owner(s). If consent for reproduction or disclosure in whole or in part is given, this notice shall be set forth on each document page and/or in each electronic reproduction so authorized.
Entry # | Drawing # | Located Y/N | TAG Search | DEVICE TAG NAME |  |  | REFERENCE DRAWING No. | FUNCTIONAL DESCRIPTION | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONSTRUCTION NOTES
|  |  |  | DEVICE CODE | EQUIP. CODE | ID CODE
1 | 8 | Y | FCV IAS 101 | FCV | IAS | 101 | 9517-PID-101a | Flow Control Valve for (FCV-TANK1-101) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
2 | 12 | Y | FCV IAS 101 | FCV | IAS | 101 | 9517-PID-101a | Flow Control Valve for (FCV-TANK1-102) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
3 | 20 | Y | FCV IAS 101 | FCV | IAS | 101 | 9517-PID-101a | Flow Control Valve for (FCV-TANK1-103) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
4 | 9 | Y | FCV IAS 101 | FCV | IAS | 101 | 9517-PID-101a | Flow Control Valve for (FCV-TANK2-101) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
5 | 13 | Y | FCV IAS 101 | FCV | IAS | 101 | 9517-PID-101a | Flow Control Valve for (FCV-TANK2-102) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
6 | 21 | Y | FCV IAS 101 | FCV | IAS | 101 | 9517-PID-101a | Flow Control Valve for (FCV-TANK2-103) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
7 | 28 | Y | FCV IAS 102 | FCV | IAS | 102 | 9517-PID-101a | IAS Solenoid Valve for Tank #1 | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
8 | 29 | Y | FCV IAS 103 | FCV | IAS | 103 | 9517-PID-101a | IAS Solenoid Valve for Tank #2 | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
9 | 32 | Y | FCV IAS 104 | FCV | IAS | 104 | 9517-PID-101a | IAS Solenoid Valve for (FCV-NG-103) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
10 | 33 | Y | FCV IAS 105 | FCV | IAS | 105 | 9517-PID-101b | Flow Control Valve for (FCV-NG-103) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
11 | 10 | Y | HV IAS 101 | HV | IAS | 101 | 9517-PID-101a | Vented Ball Valve for (FCV-TANK1-101) | 0.25 | 0.25 | FNPT | Apollo | 7K-101-27 | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
12 | 52 | Y | HV IAS 101 | HV | IAS | 101 | 9517-PID-101b | Vented Ball Valve for (FCV-TANK1-102) | 0.25 | 0.25 | FNPT | Apollo | 7K-101-27 | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
13 | 24 | Y | HV IAS 101 | HV | IAS | 101 | 9517-PID-101a | Vented Ball Valve for (FCV-TANK1-103) | 0.25 | 0.25 | FNPT | Apollo | 7K-101-27 | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
14 | 11 | Y | HV IAS 101 | HV | IAS | 101 | 9517-PID-101a | Vented Ball Valve for (FCV-TANK2-101) | 0.25 | 0.25 | FNPT | Apollo | 7K-101-27 | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
15 | 19 | Y | HV IAS 101 | HV | IAS | 101 | 9517-PID-101a | Vented Ball Valve for (FCV-TANK2-102) | 0.25 | 0.25 | FNPT | Apollo | 7K-101-27 | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
16 | 25 | Y | HV IAS 101 | HV | IAS | 101 | 9517-PID-101a | Vented Ball Valve for (FCV-TANK2-103) | 0.25 | 0.25 | FNPT | Apollo | 7K-101-27 | 1/4” Brass Ball Valve w/ Drain, SS Latch Lock Lever and Nut
17 | 64 | Y | HV IAS 102 | HV | IAS | 102 | 9517-PID-101b | Vented Ball Valve for (FCV-NG-103) | 0.25 | 0.25 | FNPT | RUB | S93B41 | 1/4” Brass Ball Valve, Vented
18 | 35 | Y | FCV NG 101 | FCV | NG | 101 | 9517-PID-101b | Natural Gas Pad Check Valve #1 | 2 | 2 | ANSI 150# | Wheatley | 510-025027-121 | Carbon Steel Flanged End Check Valve, Raised Face
19 | 69 | Y | FCV NG 102 | FCV | NG | 102 | 9517-PID-101b | Natural Gas Pad Check Valve #2 | 2 | 2 | ANSI 150# | Wheatley | 510-025027-121 | Carbon Steel Flanged End Check Valve, Raised Face
20 | 38 | Y | FCV NG 103 | FCV | NG | 103 | 9517-PID-101b | Natural Gas Pad Actuated Ball Valve | 2 | 2 | ANSI 150# | Kuka/Triac | CBA15BGLN/2R200SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
21 | 36 | Y | HV NG 101 | HV | NG | 101 | 9517-PID-101b | Natural Gas Pad Inlet Ball Valve | 2 | 2 | ANSI 150# | Kuka | CBA15BGLN | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim
22 | 66 | Y | HV NG 102 | HV | NG | 102 | 9517-PID-101b | Natural Gas Pad Gauge Isolation Valve # 1 | 0.5 | 0.5 | MNPT x FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
23 | 67 | Y | HV NG 103 | HV | NG | 103 | 9517-PID-101b | Natural Gas Pad Gauge Isolation Valve # 2 | 0.5 | 0.5 | MNPT x FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
24 | 37 | Y | PCV NG 101 | PCV | NG | 101 | 9517-PID-101b | Natural Gas Pad Pressure Regulator | 1 | 1 | FNPT | Fisher | 627 | Steel body, 1/4" orifice, 70-150 psig Spring Range
25 | 34 | Y | PI NG 101 | PI | NG | 101 | 9517-PID-101b | Natural Gas Pad Pressure Indicator | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4.5" Dial, 1/2" Lower Mount, 0-200 Psig Range
26 | 65 | Y | PI NG 102 | PI | NG | 102 | 9517-PID-101b | Natural Gas Pad Pressure Indicator | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4.5" Dial, 1/2" Lower Mount, 0-200 Psig Range
27 | 68 | Y | HV TA 105 | HV | TA | 105 | 9517-PID-101b | Propane Vapor Line 3-Way Ball Valve for Hydrostatic Relief Valves | 0.5 | 0.5 | FNPT | Apollo | 76-603 | 3-Way, SS Body, and Trim
28 | 56 | Y | HV TA 106 | HV | TA | 106 | 9517-PID-101b | Propane Vapor Line 3-Way Ball Valve for Hydrostatic Relief Valves | 0.5 | 0.5 | FNPT | Apollo | 76-603 | 3-Way, SS Body, and Trim
29 | 23 | Y | HV TA 107 | HV | TA | 107 | 9517-PID-101a | Propane Liquid Line 3-Way Ball Valve for Hydrostatic Relief Valves | 0.5 | 0.5 | FNPT | Apollo | 76-603 | 3-Way, SS Body, and Trim
30 | 71 | Y | PSV TA 101 | PSV | TA | 101 | 9517-PID-101b | Natural Gas Hydrostatic Relief Valve # 1 | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
31 | 70 | Y | PSV TA 102 | PSV | TA | 102 | 9517-PID-101b | Natural Gas Hydrostatic Relief Valve # 2 | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
32 | 27 | Y | PSV TA 103 | PSV | TA | 103 | 9517-PID-101a | Propane Vapor Line Hydrostatic Relief Valve # 1 | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
33 | 55 | Y | PSV TA 104 | PSV | TA | 104 | 9517-PID-101b | Propane Vapor Line Hydrostatic Relief Valve # 2 | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
34 | 54 | Y | PSV TA 105 | PSV | TA | 105 | 9517-PID-101b | Propane Liquid Line Hydrostatic Relief Valve # 1 | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
35 | 53 | Y | PSV TA 106 | PSV | TA | 106 | 9517-PID-101b | Propane Liquid Line Hydrostatic Relief Valve # 2 | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Releif Valve w 3129-10 Pipe Away
36 | 14 | Y | FCV TANK1 101 | FCV | TANK1 | 101 | 9517-PID-101a | Actuated Internal Valve - Propane Liquid Out Line, Propane Storage Tank No. 1 | 3 | 3 | MNPT/FNPT | Rego | A3213R300 w/ A3213PA | ~300 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
37 | 15 | Y | FCV TANK1 102 | FCV | TANK1 | 102 | 9517-PID-101a | Actuated Internal Valve - Propane Liquid Fill Line, Propane Storage Tank No. 1 | 2 | 2 | MNPT/FNPT | Rego | A3212R250 w/A3213PA | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
38 | 16 | Y | FCV TANK1 103 | FCV | TANK1 | 103 | 9517-PID-101a | Actuated Internal Valve - Propane Vapor Line, Propane Storage Tank No. 1 | 2 | 2 | MNPT/FNPT | Rego | A3212R250 w/A3213PA | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
39 | 61 | Y | HV TANK1 101 | HV | TANK1 | 101 | 9517-PID-101b | Isolation Ball Valve - Liquid Out Line, Propane Storage Tank No. 1 | 3 | 3 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
40 | 62 | Y | HV TANK1 102 | HV | TANK1 | 102 | 9517-PID-101b | Isolation Ball Valve - Liquid Fill Line Propane, Storage Tank No. 1 | 2 | 2 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
41 | 58 | Y | HV TANK1 103 | HV | TANK1 | 103 | 9517-PID-101b | Isolation Ball Valve - Natural Gas Line, Propane Storage Tank No. 1 | 2 | 2 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
42 | 59 | Y | HV TANK1 104 | HV | TANK1 | 104 | 9517-PID-101b | Isolation Ball Valve - Propane Vapor Line Propane Storage Tank No. 1 | 2 | 2 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
43 | 41 | Y | HV TANK1 105 | HV | TANK1 | 105 | 9517-PID-101b | Instrument Isolation Valve for LI TANK1 102, Propane Storage Tank No. 1 | 0.25 | 0.25 | MNPT x FNPT | Anderson Greenwood | H5VIS22A | 1/4" SS Angle Needle Valve, w/ T Handle
44 | 48 | Y | HV TANK1 106 | HV | TANK1 | 106 | 9517-PID-101b | Instrument Isolation Valve for PI & PT TANK1 101, Propane Storage Tank No. 1 | 0.25 | 0.25 | MNPT x FNPT | Anderson Greenwood | H5VIS22A | 1/4" SS Angle Needle Valve, w/ T Handle
45 | 49 | Y | LI TANK1 101 | LI | TANK1 | 101 | 9517-PID-101b | Level Indicator for Propane Storage Tank No. 1 | 2.5 | NA | MNPT | Taylor | ME3862B / 5331 Adapter | 11' Diameter Tank Master LP End Mount, 8" Dial
46 | 43 | Y | LI TANK1 102 | LI | TANK1 | 102 | 9517-PID-101b | 85% Spit Valve to be Installed on (HV-TANK1-105) | 0.25 | NA | MNPT | Marshall Excelsior | MEJ402S | 85% Bleeder to be installed on H5VIS22A
47 | 40 | Y | LT TANK1 101 | LT | TANK1 | 101 | 9517-PID-101b | Liquid Level Transmitter for Propane Storage Tank No. 1 | 0.75 | NA | MNPT | MTS | MRA2B1B11A1U110.00S | 110" Order Length, 3/4" MNPT, Calibrated 4" to 108.25", -30 to 150 F
48 | 46 | Y | PI TANK1 101 | PI | TANK1 | 101 | 9517-PID-101b | Pressure Indicator for Propane Storage Tank No. 1 | 0.25 | NA | MNPT | Trerice | 450SS4502LA140 | 4.5" Dial, 1/4" LM Connection, 0-300 Psig Range, SS
49 | 44 | Y | PT TANK1 101 | PT | TANK1 | 101 | 9517-PID-101b | Pressure Indicating Transmitter for Propane Storage Tank No. 1 | 0.5 | NA | MNPT | Wika | E-10 # 4365182 | 0-300 Psig Scale, Explosion Proof, Wire End
50 | 50 | Y | TI TANK1 101 | TI | TANK1 | 101 | 9517-PID-101b | Temperature Indicator for Tank No. 1 | 0.5 | NA | MNPT | Tel-Tru | GT-300R | -40 to 160 Deg F, 6" Stem
51 | 39 | Y | TT TANK1 101 | TT | TANK1 | 101 | 9517-PID-101b | Temperature Transmitter for Tank No. 1 | NA | NA | NA | MTS | Part of LT-T1-101 | Internal Temp Transmitter (see LT-TI-101)
52 | 3 | Y | TW TANK1 101 | TW | TANK1 | 101 | 9517-PID-101a | Themowell Included (LT-TANK1-101) | 0.75 | 0.75 | MNPT x FNPT | MTS | Part of LT-TI-101 | Thermowell (see LT-TI-101)
53 | 17 | Y | FCV TANK2 101 | FCV | TANK2 | 101 | 9517-PID-101a | Actuated Internal Valve - Propane Liquid Out Line, Propane Storage Tank No. 2 | 3 | 3 | MNPT/FNPT | Rego | A3213R300 w/ A3213PA | ~300 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
54 | 18 | Y | FCV TANK2 102 | FCV | TANK2 | 102 | 9517-PID-101a | Actuated Internal Valve - Propane Liquid Fill Line, Propane Storage Tank No. 2 | 2 | 2 | MNPT/FNPT | Rego | A3212R250 w/A3213PA | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
55 | 51 | Y | FCV TANK2 103 | FCV | TANK2 | 103 | 9517-PID-101b | Actuated Internal Valve - Propane Vapor Line, Propane Storage Tank No. 2 | 2 | 2 | MNPT/FNPT | Rego | A3212R250 w/A3213PA | ~250 GPM Liquid Propane Close Rate, NPT Internal Valve w/ Actuator
56 | 57 | Y | HV TANK2 101 | HV | TANK2 | 101 | 9517-PID-101b | Isolation Ball Valve - Liquid Out Line, Propane Storage Tank No. 2 | 3 | 3 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
57 | 63 | Y | HV TANK2 102 | HV | TANK2 | 102 | 9517-PID-101b | Isolation Ball Valve - Liquid Fill Line Propane, Storage Tank No. 2 | 2 | 2 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
58 | 60 | Y | HV TANK2 103 | HV | TANK2 | 103 | 9517-PID-101b | Isolation Ball Valve - Natural Gas Line, Propane Storage Tank No. 2 | 2 | 2 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
59 | 30 | Y | HV TANK2 104 | HV | TANK2 | 104 | 9517-PID-101a | Isolation Ball Valve - Propane Vapor Line Propane Storage Tank No. 2 | 2 | 2 | ANSI 300# | Kuka | CBA30BG | Full Port Fire Rated Carbon Steel Body, Stainless Steel Trim
60 | 5 | Y | HV TANK2 105 | HV | TANK2 | 105 | 9517-PID-101a | Combo Valve for Propane Storage Tank No. 2 | 0.75 | 0.25 | MNPT x FNPT | Marshall Excelsior | MEJ415 | Combo Valve for 85% Bleed Valve, Pressure Gauge
61 | 47 | Y | LI TANK2 101 | LI | TANK2 | 101 | 9517-PID-101b | Level Indicator for Propane Storage Tank No. 2 | 2.5 | NA | MNPT | Taylor | ME3862B / 5331 Adapter | 11' Diameter Tank Master LP End Mount, 8" Dial
62 | 6 | Y | LI TANK2 102 | LI | TANK2 | 102 | 9517-PID-101a | 85% Spit Valve to be Installed on (HV-TANK2-105) | 0.25 | NA | MNPT | Marshall Excelsior | MEJ402S | 85% Bleeder to be installed on MEJ415
63 | 2 | Y | LT TANK2 101 | LT | TANK2 | 101 | 9517-PID-101a | Liquid Level Transmitter for Propane Storage Tank No. 2 | 0.75 | NA | MNPT | MTS | MRA2B1B11A1U110.00S | 110" Order Length, 3/4" MNPT, Calibrated 4" to 108.25", -30 to 150 F
64 | 42 | Y | PI TANK2 101 | PI | TANK2 | 101 | 9517-PID-101b | Pressure Indicator for Propane Storage Tank No. 2 | 0.25 | NA | MNPT | Trerice | 450SS4502LA140 | 4.5" Dial, 1/4" LM Connection, 0-300 Psig Range, SS
65 | 45 | Y | PT TANK2 101 | PT | TANK2 | 101 | 9517-PID-101b | Pressure Indicating Transmitter for Propane Storage Tank No.2 | 0.5 | NA | MNPT | Wika | E-10 # 4365182 | 0-300 Psig Scale, Explosion Proof, Wire End
66 | 7 | Y | TI TANK2 101 | TI | TANK2 | 101 | 9517-PID-101a | Temperature Indicator for Tank No. 2 | 0.5 | NA | MNPT | Tel-Tru | GT-300R | -40 to 160 Deg F, 6" Stem
67 | 1 | Y | TT TANK2 101 | TT | TANK2 | 101 | 9517-PID-101a | Temperature Transmitter for Tank No. 2 | NA | NA | NA | MTS | Part of LT-T2-101 | Internal Temp Transmitter (see LT-TI-101)
68 | 4 | Y | TW TANK2 101 | TW | TANK2 | 101 | 9517-PID-101a | Themowell Included (LT-TANK2-101) | 0.75 | 0.75 | MNPT x FNPT | MTS | Part of LT-T2-101 | Thermowell (see LT-TI-101)
69 | 26 | Y | FCV VAP 102 | FCV | VAP | 102 | 9517-PID-101a | Propane Vapor to Blender Discharge Check Valve | 1 | 1 | FNPT | Wheatley | 822-013072-131 | CS Body, SS Clapper, 720# Working Pressure
70 | 31 | Y | HV VAP 103 | HV | VAP | 103 | 9517-PID-101a | Propane Vapor to Blender Discharge Isolation Ball Valve | 1 | 1 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body and Trim, Fire Safe
71 | 22 | Y | PSV VAP 101 | PSV | VAP | 101 | 9517-PID-101a | Propane Vapor to Blender Hydrostatic Relief Valve | 0.5 | 0.5 | MNPT | Rego | 3129U w/ 3129-10 | 450 Psig Hydrostatic Relief Valve w 3129-10 Pipe Away
| 72 | Y | PRV T1 1 | PRV | T1 | 1 | 9517-PID-101a | Tank 001 Primary Relief Valve #1
| 73 | Y | PRV T1 2 | PRV | T1 | 2 | 9517-PID-101a | Tank 001 Primary Relief Valve #2
| 74 | Y | PRV T1 3 | PRV | T1 | 3 | 9517-PID-101a | Tank 001 Primary Relief Valve #3
| 75 | Y | PRV T1 4 | PRV | T1 | 4 | 9517-PID-101a | Tank 001 Primary Relief Valve #4
| 76 | Y | PRV T2 1 | PRV | T2 | 1 | 9517-PID-101a | Tank 002 Primary Relief Valve #1
| 77 | Y | PRV T2 2 | PRV | T2 | 2 | 9517-PID-101a | Tank 002 Primary Relief Valve #2
| 78 | Y | PRV T2 3 | PRV | T2 | 3 | 9517-PID-101a | Tank 002 Primary Relief Valve #3
| 79 | Y | PRV T2 4 | PRV | T2 | 4 | 9517-PID-101a | Tank 002 Primary Relief Valve #4
Note on O77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Corrected misspelling of "relief"

## 12023-PID-102-R03
|  |  |  | PROJECT: |  | Berkshire Gas Co. |  |  |  |  | FILE DATE: | 5/7/2012
|  |  |  | JOB NUMBER: |  | 12023 |  |  |  |  | REVISION DATE: | 7/13/18
|  |  |  | REF. DRAWING: |  | 12023-PID-103-R3 |  |  |  |  | PRINT DATE: | 5/31/19
The information contained in this document and/or electronic file(s) is proprietary and/or confidential property Standby Systems, Inc. and shall not be used, reproduced or disclosed to others without the express written consent of the respective owner(s). If consent for reproduction or disclosure in whole or in part is given, this notice shall be set forth on each document page and/or in each electronic reproduction so authorized.
Entry # | Drawing # | Located Y/N | TAG Search | DEVICE TAG NAME |  |  | REFERENCE DRAWING No. | FUNCTIONAL DESCRIPTION | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONSTRUCTION NOTES
|  |  |  | DEVICE CODE | EQUIP. CODE | ID CODE
1 | 1 | Y | HV AIR 105 | HV | AIR | 105 | 12023-PID-102-R03 | Process Air Compressor Discharge Isolation Valve | 3 | 3 | ANSI 150# | Kuka | CBA15BGLN | Carbon Steel Body, SS Trim, Fire Safe, Full Port
1 | 2 | Y | HV AIR 104 | HV | AIR | 104 | 12023-PID-102-R03 | Process Air Compressor Discharge Isolation Valve | 3 | 3 | ANSI 150# | Kuka | CBA15BGLN | Carbon Steel Body, SS Trim, Fire Safe, Full Port
4 | 3 | Y | PE AIR 101 | PE | AIR | 101 | 12023-PID-102-R03 | Process Air Compressor No, 2 | NA | 3 | FNPT | Atlas Copco | GA110-6.9-60 | Oil Injected 150 HP Rotary Screw, 747 SCFM @ 90 psig Capacity
6 | 4 | Y | PI AIR 101 | PI | AIR | 101 | 12023-PID-102-R03 | Process Air Tank Pressure Indicator | 0.5 | 0.5 | MNPT | US Gauge | 1981 # 150027DM | 4.5" Dial, 1/2" Lower Mount, Dry, 0-200 Psig Range
3 | 5 | Y | HV AIR 103 | HV | AIR | 103 | 12023-PID-102-R03 | Process Air Tank Instrument Isolation Valve | 0.5 | 0.5 | MXFNPT | Dragon | 10M517G | CS Bar Stock Body - 6000 psig Max
7 | 6 | Y | PSV AIR 101 | PSV | AIR | 101 | 12023-PID-102-R03 | Process Air Tank Relief Valve | 1" | 1/2" | MNPT x FNPT | Kunkle | 6283FEV01 | 978 SCFM Capacity, up to 406 Deg F, 150 Psig Setting
2 | 7 | Y | HV AIR 102 | HV | AIR | 102 | 12023-PID-102-R03 | Process Air Tank Drain Valve | 1 | 1 | FNPT | RUB | S92EB8 | 1" Non-Vented Brass Ball Valve
5 | 8 | Y | PE AIR 102 | PE | AIR | 102 | 12023-PID-102-R03 | Process Air Compressor | 3 | 3 | ANSI 150# | Sylvin Tank | TBD | 620 Gallon, 3" 150# Flange Connection, ASME
16 | 9 | Y | TT AIR 102 | TT | AIR | 102 | 12023-PID-102-R03 | Process Air Tank No.2 | 1 | 2 | FNPT | Algas-SDI | Q1650V | 1650 GPH Liquid Propane Vaporizer
1 | 10 | Y | HV AIR 101 | HV | AIR | 101 | 12023-PID-102-R03 | Process Air Compressor Discharge Isolation Valve | 3 | 3 | ANSI 150# | Kuka | CBA15BGLN | Carbon Steel Body, SS Trim, Fire Safe, Full Port
4 | 11 | Y | PE AIR 101 | PE | AIR | 101 | 12023-PID-102-R03 | Process Air Compressor No. 1 | NA | 3 | FNPT | Atlas Copco | GA110-6.9-60 | Oil Injected 150 HP Rotary Screw, 747 SCFM @ 90 psig Capacity
21 | 12 |  | TT AIR 101 | TT | AIR | 101 | 12023-PID-102-R03 | Process Air Tank No.1 |  |  |  |  | GA110-6.9-60 | 480 VAC 150 HP
14 | 13 | Y | PA VAP 101 | PA | VAP | 101 | 12023-PID-102-R03 | Vaporizer Relief Stack Cap | 2 | NA | NA | Anthes Weather Cap | WC 5 | Weather Cap
15 | 14 | Y | PA VAP 102 | PA | VAP | 102 | 12023-PID-102-R03 | Vaporizer Relief Valve Pipe Away Adapter | 1.25 | 2 | NPT | Rego | 3135-10 | Relief Valve Pipe Away Adapter
17 | 15 | Y | PT VAP 101 | PT | VAP | 101 | 12023-PID-102-R03 | Vaporizer Outlet Pressure Transmitter | 0.5 | NA | FNPT | Wika | E-10 # 4365182 | 0-300 Psig Scale, Explosion Proof
13 | 16 | Y | HV VAP 102 | HV | VAP | 102 | 12023-PID-102-R03 | Instrument Isolation Ball Valve | 0.5 | 0.5 | MNPT x FNPT | Dragon | 10M517G | CS Bar Stock Body - 6000 psig Max
18 | 17 | Y | RTD VAP 101 | RTD | VAP | 101 | 12023-PID-102-R03 | Vaporizer Outlet Resistive Temperature Device | 0.5 | NA | FNPT | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
19 | 18 | Y | TW VAP 101 | TW | VAP | 101 | 12023-PID-102-R03 | Vaporizer Outlet Thermowell for Temperature Transmitter | 0.5 | NA | FNPT | Pyromation | Part of RTD- VAP-101 | 1/2" Connection, 2.5" Insertion Length
11 | 19 | Y | FCV VAP 101 | FCV | VAP | 101 | 12023-PID-102-R03 | Vaporizer Discharge Actuated Ball Valve | 3 | 3 | ANSI 300# | Kuka/Triac | CBA30BGLN/2R300SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
8 | 20 | Y | FCV IAS 122 | FCV | IAS | 122 | 12023-PID-102-R03 | IAS Solenoid Valve for (FCV-VAP-101) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
9 | 21 | Y | FCV IAS 123 | FCV | IAS | 123 | 12023-PID-102-R03 | IAS Flow Control Valve for (FCV-VAP-101) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
10 | 22 | Y | HV IAS 118 | HV | IAS | 118 | 12023-PID-102-R03 | IAS Vented Ball Valve for (FCV-VAP-101) | 0.25 | 0.25 | FNPT | RUB | S93B41 | 1/4” Brass Ball Valve, Vented
16 | 23 | Y | PE VAP 101 | PE | VAP | 101 | 12023-PID-102-R03 | Q1650V Vertical Waterbath Vaporizer 1 | 1 | 2 | FNPT | Algas-SDI | Q1650V | 1650 GPH Liquid Propane Vaporizer
20 | 24 | Y | HV VAP 103 | HV | VAP | 103 | 12023-PID-102-R03 | Vaporizer 1 Inlet Isolation Ball Valve | 2 | 2 | ANSI 300# | Titan | YS-62-CS | Carbon Steel Body, SS 40 Mesh Strainer
20 | 25 | Y | ST VAP 101 | ST | VAP | 101 | 12023-PID-102-R03 | Vaporizer Inlet Strainer | 2 | 2 | ANSI 300# | Titan | YS-62-CS | Carbon Steel Body, SS 40 Mesh Strainer
12 | 26 | Y | HV VAP 101 | HV | VAP | 101 | 12023-PID-102-R03 | Vaporizer Inlet Isolation Ball Valve | 2 | 2 | ANSI 300# | Kuka | CBA30BGLN | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim
8 | 27 | Y | FCV IAS 106 | FCV | IAS | 106 | 12023-PID-102-R03 | IAS Solenoid Valve for (FCV-VAP-102) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
9 | 28 | Y | FCV IAS 107 | FCV | IAS | 107 | 12023-PID-102-R03 | IAS Flow Control Valve for (FCV-VAP-102) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
10 | 29 | Y | HV IAS 104 | HV | IAS | 104 | 12023-PID-102-R03 | IAS Vented Ball Valve for (FCV-VAP-102) | 0.25 | 0.25 | FNPT | RUB | S93B41 | 1/4” Brass Ball Valve, Vented
14 | 30 | Y | PA VAP 103 | PA | VAP | 103 | 12023-PID-102-R03 | Vaporizer Relief Stack Cap | 2 | NA | NA | Anthes Weather Cap | WC 5 | Weather Cap
15 | 31 | Y | PA VAP 104 | PA | VAP | 104 | 12023-PID-102-R03 | Vaporizer Relief Valve Pipe Away Adapter | 1.25 | 2 | NPT | Rego | 3135-10 | Relief Valve Pipe Away Adapter
17 | 32 | Y | PT VAP 102 | PT | VAP | 102 | 12023-PID-102-R03 | Vaporizer Outlet Pressure Transmitter | 0.5 | NA | FNPT | Wika | E-10 # 4365182 | 0-300 Psig Scale, Explosion Proof
13 | 33 | Y | HV VAP 105 | HV | VAP | 105 | 12023-PID-102-R03 | Instrument Isolation Ball Valve | 0.5 | 0.5 | MNPT x FNPT | Dragon | 10M517G | CS Bar Stock Body - 6000 psig Max
18 | 34 | Y | RTD VAP 102 | RTD | VAP | 102 | 12023-PID-102-R03 | Vaporizer Outlet Resistive Temperature Device | 0.5 | NA | FNPT | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
19 | 35 | Y | TW VAP 102 | TW | VAP | 102 | 12023-PID-102-R03 | Vaporizer Outlet Thermowell for Temperature Transmitter | 0.5 | NA | FNPT | Pyromation | Part of RTD- VAP-101 | 1/2" Connection, 2.5" Insertion Length
11 | 36 | Y | FCV VAP 102 | FCV | VAP | 102 | 12023-PID-102-R03 | Vaporizer Discharge Actuated Ball Valve | 3 | 3 | ANSI 300# | Kuka/Triac | CBA30BGLN/2R300SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
16 | 37 | Y | PE VAP 102 | PE | VAP | 102 | 12023-PID-102-R03 | Q1650V Vertical Waterbath Vaporizer 2 | 1 | 2 | FNPT | Algas-SDI | Q1650V | 1650 GPH Liquid Propane Vaporizer
12 | 38 | Y | HV VAP 104 | HV | VAP | 104 | 12023-PID-102-R03 | Vaporizer 2 Inlet Isolation Ball Valve | 2 | 2 | ANSI 300# | Kuka | CBA30BGLN | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim
16 | 39 | Y | PSV VAP 101 | PSV | VAP | 101 | 12023-PID-102-R03 | Vaporizer Inlet Pressure Relief Valve | 1 | 2 | FNPT | Algas-SDI | Q1650V | 1650 GPH Liquid Propane Vaporizer

## 9517-PID-103
|  |  |  | PROJECT: |  | Berkshire Gas Co. |  |  |  |  | FILE DATE: | 5/7/2012
|  |  |  | JOB NUMBER: |  | 9517 |  |  |  |  | REVISION DATE: | 7/23/2012
|  |  |  | REF. DRAWING: |  | 9517-PID-103 |  |  |  |  | PRINT DATE: | 1/29/2013 10:56
The information contained in this document and/or electronic file(s) is proprietary and/or confidential property Standby Systems, Inc. and shall not be used, reproduced or disclosed to others without the express written consent of the respective owner(s). If consent for reproduction or disclosure in whole or in part is given, this notice shall be set forth on each document page and/or in each electronic reproduction so authorized.
Entry # | Drawing # | Located Y/N | TAG Search | DEVICE TAG NAME |  |  | REFERENCE DRAWING No. | FUNCTIONAL DESCRIPTION | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONSTRUCTION NOTES
|  |  |  | DEVICE CODE | EQUIP. CODE | ID CODE
1 | 11 | Y | ESV FTS 101 | ESV | FTS | 101 | 9517-PID-103a | Emergency Shutoff Valve | 1.25 | 1.25 | FNPT | Fisher | N550 w/ P327D | Emergency Shutoff Valve w/ Pneumatic Release
2 | 7 | Y | FCV FTS 101 | FCV | FTS | 101 | 9517-PID-103a | Flow Control Valve (FTS Liquid Line) | 2 | 2 | FNPT | Wheatley | 822-023072-131 | Check Valve - Carbon Steel Body/ SS Clapper
3 | 15 | Y | FCV FTS 102 | FCV | FTS | 102 | 9517-PID-103a | Flow Control Valve (FTS Vapor Line) | 1.25 | 1.25 | FNPT | Fisher | 105 | Excess Flow Valve
4 | 2 | Y | HV FTS 101 | HV | FTS | 101 | 9517-PID-103a | Angle Valve (FTS Liquid Line) | 2 | 2 | FNPT | Squib-Taylor | AL317P | 2" Angle Style Globe Valve
5 | 8 | Y | HV FTS 102 | HV | FTS | 102 | 9517-PID-103a | Strainer Blow Down Valve | 1 | 1 | FNPT | Jamesbury | 9FB3600XT | Fire Safe, Stainless Steel Body, Stainless Steel Trim
6 | 3 | Y | HV FTS 103 | HV | FTS | 103 | 9517-PID-103a | Isolation Ball Valve (FTS Liquid Line) | 2 | 2 | FNPT | Jamesbury | 9FB3600XT | Fire, Safe, Stainless Steel Body, Stainless Steel Trim
7 | 10 | Y | HV FTS 104 | HV | FTS | 104 | 9517-PID-103a | Angle Valve (FTS Vapor Line) | 1.25 | 1.25 | FNPT | Squibb-Taylor | AL313P | 1.25" Angle Style Globe Valve
8 | 12 | Y | HV FTS 105 | HV | FTS | 105 | 9517-PID-103a | Isolation Ball Valve (FTS Vapor Line) | 2 | 2 | FNPT | Jamesbury | 9FB3600XT | Fire Safe, Stainless Steel Body, Stainless Steel Trim
9 | 14 | YY | PE FTS 101 | PE | FTS | 101 | 9517-PID-103a | FTS Bulkhead | 1.25 | 2 | FNPT | Standby Systems | SSI Drawing | Engineered Breakaway Risers
10 | 1 | Y | PE FTS 102 | PE | FTS | 102 | 9517-PID-103a | Liquid Acme Fill Adapter (FTS Liquid Line) | 2 | 3.25 | MNPT/ACME | Fisher | ME503-16, ME441F-1 | 3-1/4" Acme X 2" NPT Acme Adapter/ Cap & Chain
11 | 9 | Y | PE FTS 104 | PE | FTS | 104 | 9517-PID-103a | Vapor Acme Fill Adapter (FTS Vapor Line) | 1.25 | 2.25 | MNPT/ACME | Fisher | ME233, ME431F-1 | 2-1/4" Acme X 1 1/4" NPT Acme Adapter/ Cap & Chain
12 | 4 | Y | PSV FTS 101 | PSV | FTS | 101 | 9517-PID-103a | Hydrostatic Relief Valve (FTS Liquid Line) | 0.25 | NA | MNPT | Rego | 3125L | 400 Psig Hydrostatic Relief Valve
13 | 13 | Y | PSV FTS 103 | PSV | FTS | 103 | 9517-PID-103a | Hydrostatic Relief Valve (FTS Vapor Line) | 0.25 | NA | MNPT | Rego | 3125L | 400 Psig Hydrostatic Relief Valve
14 | 5 | Y | ST FTS 101 | ST | FTS | 101 | 9517-PID-103a | Strainer for (Liquid Fill Line) | 2 | 2 | FNPT | Titan | YS-81 CS | Carbon Steel Body w/ 40Mesh Screen
15 | 16 | Y | HV IAS 105 | HV | IAS | 105 | 9517-PID-103a | Pneumatic Isolation for ESV Valve | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4" Brass Ball Valve, Vented
9 | 6 | YY | PE FTS 101 | PE | FTS | 101 | 9517-PID-103a | FTS Bulkhead | 1.25 | 2 | FNPT | Standby Systems | SSI Drawing | Engineered Breakaway Risers
Note on C15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should one of these be PE FTS 103?
Note on C22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should one of these be PE FTS 103?

## 9517-PID-104
|  |  |  | PROJECT: |  | Berkshire Gas Co. |  |  |  |  | FILE DATE: | 7/25/2012
|  |  |  | JOB NUMBER: |  | 9517 |  |  |  |  | REVISION DATE: | 8/9/2012
|  |  |  | REF. DRAWING: |  | 9517-PID-104 |  |  |  |  | PRINT DATE: | 1/29/2013 10:57
The information contained in this document and/or electronic file(s) is proprietary and/or confidential property Standby Systems, Inc. and shall not be used, reproduced or disclosed to others without the express written consent of the respective owner(s). If consent for reproduction or disclosure in whole or in part is given, this notice shall be set forth on each document page and/or in each electronic reproduction so authorized.
Entry # | Drawing # | Located Y/N | TAG Search | DEVICE TAG NAME |  |  | REFERENCE DRAWING No. | FUNCTIONAL DESCRIPTION | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONSTRUCTION NOTES
|  |  |  | DEVICE CODE | EQUIP. CODE | ID CODE
1 | 1 | Y | FCV IAS 119 | FCV | IAS | 119 | 9517-PID-104a | Instrument Air Main Soleniod Valve | 0.5 | 0.5 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
2 | 6 | Y | HV IAS 115 | HV | IAS | 115 | 9517-PID-104a | Instrument Air Compressor Discharge Valve | 0.5 | 0.5 | FNPT | RUB | S92DB8 | Non-Vented 1/2" Brass Ball Valve
3 | 7 | Y | HV IAS 116 | HV | IAS | 116 | 9517-PID-104a | Instrument Air Isolation Ball Valve | 0.5 | 0.5 | FNPT | RUB | S92DB8 | Non-Vented 1/2" Brass Ball Valve
4 | 8 | Y | PCV IAS 101 | PCV | IAS | 101 | 9517-PID-104a | Instrument Air Regulator | 0.25 | 0.25 | NPT | Control-Air | 300-BC | Pressure Regulator, Set 70-80 psig
5 | 10 | Y | PCV IAS 102 | PCV | IAS | 102 | 9517-PID-104a | Instrument Air Regulator | 0.25 | 0.25 | NPT | Control-Air | 300-BC | Pressure Regulator, Set 30-35 psig
6 | 4 | Y | PE IAS 101 | PE | IAS | 101 | 9517-PID-104a | Instrument Air Compressor | NA | NA | NA | Atlas Copco | GX2-150 | 3 HP, 480 VAC 3 phase, 60HZ, capable of 8.5 SCFM, Tank Mounted w/ disconntect swtich
7 | 5 | Y | PE IAS 102 | PE | IAS | 102 | 9517-PID-104a | IAS Dryer and Filter | 0.25 | 0.25 | FNPT | Stylair | H12N | 10 SCFM Capacity, -40 Deg. Dew Point, Pre and After Filters
8 | 2 | Y | PI IAS 101 | PI | IAS | 101 | 9517-PID-104a | Instrument Air Pressure Indicator | 0.25 | NA | FNPT | Trerice | D83SS2502LA110 | 1/4" LM, 2.5" Dial, SS Case, 0-100 Psig Range
9 | 9 | Y | PI IAS 102 | PI | IAS | 102 | 9517-PID-104a | Instrument Air Pressure Indicator | 0.25 | NA | FNPT | Trerice | D83SS2502LA110 | 1/4" LM, 2.5" Dial, SS Case, 0-100 Psig Range
10 | 3 | Y | PSL IAS 101 | PSL | IAS | 101 | 9517-PID-104a | Instrument Air Pressure Switch | 0.25 | 0.25 | FNPT | Solon | 2PSW-12 | 0-100 Psig Range, Enclosure
Note on I10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Corrected misspelling of "instrument"

## 9517-PID-105
|  |  |  | PROJECT: |  | Berkshire Gas Co. |  |  |  |  | FILE DATE: | 5/4/2012
|  |  |  | JOB NUMBER: |  | 9517 |  |  |  |  | REVISION DATE: | 9/10/2012
|  |  |  | REF. DRAWING: |  | 9517-PID-105 |  |  |  |  | PRINT DATE: | 1/29/2013 10:55
The information contained in this document and/or electronic file(s) is proprietary and/or confidential property Standby Systems, Inc. and shall not be used, reproduced or disclosed to others without the express written consent of the respective owner(s). If consent for reproduction or disclosure in whole or in part is given, this notice shall be set forth on each document page and/or in each electronic reproduction so authorized.
Entry # | Drawing # | Located Y/N | TAG Search | DEVICE TAG NAME |  |  | REFERENCE DRAWING No. | FUNCTIONAL DESCRIPTION | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONSTRUCTION NOTES
|  |  |  | DEVICE CODE | EQUIP. CODE | ID CODE
1 | 7 | Y | FCV IAS 108 | FCV | IAS | 108 | 9517-PID-105a | Control Air Solenoid Valve for (FCV-MIX-121) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
2 | 9 | Y | FCV IAS 109 | FCV | IAS | 109 | 9517-PID-105a | Control Air Flow Control Valve for (FCV-MIX-101) | 0.25 | 0.25 | FNPT | Schrader-Bellows | SPF400B | Flow Control Valve 1/4" FNPT
3 | 8 | Y | FCV IAS 110 | FCV | IAS | 110 | 9517-PID-105a | Control Air Solenoid Valve for (FCV-MIX-101) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
4 | 32 | Y | FCV IAS 111 | FCV | IAS | 111 | 9517-PID-105a | Control Air Solenoid Valve for (FCV-MIX-111) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
5 | 50 | Y | FCV IAS 112 | FCV | IAS | 112 | 9517-PID-105b | Control Air Flow Control Valve for (FCV-MIX-106) | 0.25 | 0.25 | FNPT | Schrader-Bellows | SPF400B | Flow Control Valve 1/4" FNPT
6 | 49 | Y | FCV IAS 113 | FCV | IAS | 113 | 9517-PID-105b | Control Air Solenoid Valve for (FCV-MIX-106) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
7 | 56 | Y | FCV IAS 114 | FCV | IAS | 114 | 9517-PID-105b | Control Air Flow Control Valve for (FCV-MIX-108) | 0.25 | 0.25 | FNPT | Schrader-Bellows | SPF400B | Flow Control Valve 1/4" FNPT
8 | 55 | Y | FCV IAS 115 | FCV | IAS | 115 | 9517-PID-105b | Control Air Solenoid Valve for (FCV-MIX-108) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
9 | 61 | Y | FCV IAS 116 | FCV | IAS | 116 | 9517-PID-105b | Control Air Flow Control Valve for (FCV-MIX-104) | 0.25 | 0.25 | FNPT | Schrader-Bellows | SPF400B | Flow Control Valve 1/4" FNPT
10 | 59 | Y | FCV IAS 117 | FCV | IAS | 117 | 9517-PID-105b | Control Air Solenoid Valve for (FCV-MIX-104) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
11 | 5 | Y | FCV IAS 118 | FCV | IAS | 118 | 9517-PID-105a | Control Air Solenoid Valve for (FCV-MIX-121) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
12 | 3 | Y | FCV IAS 120 | FCV | IAS | 120 | 9517-PID-105a | Control Air Solenoid Valve for (FCV-MIX-123) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
13 | 2 | Y | FCV IAS 121 | FCV | IAS | 121 | 9517-PID-105a | Control Air Flow Control Valve for (FCV-MIX-123) | 0.25 | 0.25 | FNPT | Schrader-Bellows | SPF400B | Flow Control Valve 1/4" FNPT
14 | 17 | Y | FCV MIX 101 | FCV | MIX | 101 | 9517-PID-105a | Blender Propane Vapor Inlet Actuated Ball Valve | 2 | 2 | ANSI 150# | Kuka/Triac | CBA15BGLN/2R200SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
15 | 20 | Y | FCV MIX 102 | FCV | MIX | 102 | 9517-PID-105a | Blender Propane Vapor Pressure Control Valve #2 | 2 | 2 | ANSI 150# | Fisher | V150 - V Ball | V150 W/Type 2052 Size 1 Diaphragm FO Actuator, DVC6200 Positioner, 4200 Position Transmitter
16 | 29 | Y | FCV MIX 103 | FCV | MIX | 103 | 9517-PID-105a | Propane Vapor Check Valve | 2 | 2 | ANSI 150# | Wheatley | 510-025027-121 | Carbon Steel Flanged End Check Valve, Raised Face
17 | 76 | Y | FCV MIX 104 | FCV | MIX | 104 | 9517-PID-105b | Process Air Inlet Actuated Ball Valve #1 | 2 | 2 | ANSI 150# | Kuka/Triac | CBA15BGLN/2R200SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
18 | 77 | Y | FCV MIX 106 | FCV | MIX | 106 | 9517-PID-105c | Process Air Inlet Actuated Ball Valve # 2 | 2 | 2 | ANSI 150# | Kuka/Triac | CBA15BGLN/2R200SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
19 | 93 | Y | FCV MIX 108 | FCV | MIX | 108 | 9517-PID-105c | Blender Air Supply Vent Valve (Double Block - Normally Open) | 1 | 1 | FNPT | Jamesbury/Triac | 9FB223600XT/2R200SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
20 | 89 | Y | FCV MIX 110 | FCV | MIX | 110 | 9517-PID-105c | Process Air Back Check Valve | 2 | 2 | ANSI 150# | Wheatley | 510-025027-121 | Carbon Steel Flanged End Check Valve, Raised Face
21 | 78 | Y | FCV MIX 111 | FCV | MIX | 111 | 9517-PID-105c | Process Air Pressure Control Valve | 1.5 | 1.5 | ANSI 150# | Fisher | V150 - V Ball | V150 W/Type 2052 Size 1 Diaphragm FO Actuator, DVC6200 Positioner, 4200 Position Transmitter
22 | 45 | Y | FCV MIX 121 | FCV | MIX | 121 | 9517-PID-105b | Mixed Gas Outlet AuctatedFlow Control Valve | 3 | 3 | ANSI 150# | Kuka/Triac | CBA15BGLN/2R300SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
23 | 38 | Y | FCV MIX 122 | FCV | MIX | 122 | 9517-PID-105b | Propane Vapor from Tanks Header Check Valve | 1 | 1 | FNPT | Wheatley | 822-013072-131 | CS Body, SS Clapper, 720# Working Pressure
24 | 31 | Y | FCV MIX 123 | FCV | MIX | 123 | 9517-PID-105a | Propane Vapor from Tanks Vapor Header Ball Valve | 1 | 1 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body, SS Trim, Fire Safe
25 | 66 | Y | FCV QT 101 | FCV | QT | 101 | 9517-PID-105b | Solenoid Valve Mixed Gas to S.G. Transducer | 0.25 | 0.25 | FNPT | Parker Skinner | 71216SN2FU00N0H111C2 | 2-Way, SS Body, 24VDC, Class F, 10 Watt
26 | 21 | Y | FT MIX 101 | FT | MIX | 101 | 9517-PID-105a | Blender Propane Vapor Flow Transmitter | 2 | 2 | ANSI 150# | Hoffer | HO2X2-15-CB-1MC3PAX-F1SS-X / CAT1-3/O-7-D-X | HO Series Turbine Meter w/ Cat3 Microprocessor Transmitter
27 | 79 | Y | FT MIX 102 | FT | MIX | 102 | 9517-PID-105c | Blender Process Air Supply Flow Transmitter | 2 | 2 | ANSI 150# | Hoffer | HO2X2-15-CB-1MC3PAX-F1SS-X / CAT3-2-1-1-DC-X-2/O-x | HO Series Turbine Meter w/ Cat3 Microprocessor Transmitter
28 | 6 | Y | HV IAS 108 | HV | IAS | 108 | 9517-PID-105a | Control Air Hand Valve for (FCV-MIX-121) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
29 | 10 | Y | HV IAS 109 | HV | IAS | 109 | 9517-PID-105a | Control Air Hand Valve for (FCV-MIX-101) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
30 | 33 | Y | HV IAS 110 | HV | IAS | 110 | 9517-PID-105a | Control Air Hand Valve for (FCV-MIX-111) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
31 | 51 | Y | HV IAS 111 | HV | IAS | 111 | 9517-PID-105b | Control Air Hand Valve for (FCV-MIX-106) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
32 | 54 | Y | HV IAS 112 | HV | IAS | 112 | 9517-PID-105b | Control Air Hand Valve for (FCV-MIX-108) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
33 | 60 | Y | HV IAS 113 | HV | IAS | 113 | 9517-PID-105b | Control Air Hand Valve for (FCV-MIX-104) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
34 | 4 | Y | HV IAS 114 | HV | IAS | 114 | 9517-PID-105a | Control Air Hand Valve for (FCV-MIX-121) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
35 | 1 | Y | HV IAS 117 | HV | IAS | 117 | 9517-PID-105a | Control Air Hand Valve for (FCV-MIX-123) | 0.25 | 0.25 | FNPT | Rub | S93B41 | 1/4", Vented, Brass Ball Valve
36 | 12 | Y | HV MIX 101 | HV | MIX | 101 | 9517-PID-105a | Blender Propane Supply Blowdown Valve | 0.5 | 0.5 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body, SS Trim, Fire Safe
37 | 85 | Y | HV MIX 102 | HV | MIX | 102 | 9517-PID-105c | Insturment Hand Valve for PT & PI-MIX-103 | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
38 | 18 | Y | HV MIX 103 | HV | MIX | 103 | 9517-PID-105a | Blender Propane Vapor Insturment Hand Valve for PI-MIX & PT-MIX 102 | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
39 | 26 | Y | HV MIX 105 | HV | MIX | 105 | 9517-PID-105a | Blender Air Supply Insturment Hand Valve for PI-MIX & PT-MIX-105 | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
40 | 92 | Y | HV MIX 106 | HV | MIX | 106 | 9517-PID-105c | Blender Strainer Blowdown Valve Process Air (ST-MIX-102) | 0.5 | 0.5 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body, SS Trim, Fire Safe
41 | 86 | Y | HV MIX 108 | HV | MIX | 108 | 9517-PID-105c | Blender Air Supply Insturment Hand Valve for PT & PI-MIX-104 | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
42 | 65 | Y | HV MIX 109 | HV | MIX | 109 | 9517-PID-105b | Blender Air Supply Blowdown Valve | 0.5 | 0.5 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body, SS Trim, Fire Safe
43 | 44 | Y | HV MIX 110 | HV | MIX | 110 | 9517-PID-105b | Mixer Instrument Hand Valve for PT & PI-MIX-106 | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
44 | 57 | Y | HV MIX 111 | HV | MIX | 111 | 9517-PID-105b | Hand Valve (Mixed Gas to Densitometer) | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | Carbon Steel Body, SS Trim, Fire Safe
45 | 47 | Y | HV MIX 112 | HV | MIX | 112 | 9517-PID-105b | Blender Instrument Hand Valve for PT -MIX-107 | 0.5 | 0.5 | MNPT/FNPT | Dragon | 10M517G | CS Body, Grafoil Packing - 6000 psig Max
46 | 28 | Y | HV MIX 119 | HV | MIX | 119 | 9517-PID-105a | Blowdown valve for (ST MIX 101) | 0.5 | 0.5 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body, SS Trim, Fire Safe
47 | 62 | Y | HV QT 101 | HV | QT | 101 | 9517-PID-105b | Hand Valve Test Port for Air Supply to S.G. Transducer | 0.25 | 0.25 | FNPT | Jamesbury | 9FB3600XT | Stainless Steel Body, SS Trim, Fire Safe
48 | 63 | Y | I/Z MIX 101 | I/Z | MIX | 101 | 9517-PID-105b | Current to Position Transmitter for (FCV-MIX-111) | NA | NA | NA | Fisher | DVC 6200 | Current to Position Transmitter for (FCV-MIX-111)
49 | 11 | Y | I/Z MIX 103 | I/Z | MIX | 103 | 9517-PID-105a | Current to Position Transmitter for (FCV-MIX-102) | NA | NA | NA | Fisher | DVC 6200 | Current to Position Transmitter for (FCV-MIX-102)
50 | 19 | Y | PCV MIX 101 | PCV | MIX | 101 | 9517-PID-105a | Blender Propane Vapor Pressure Control Valve #1 | 2 | 2 | ANSI 150# | Fisher | 1098-EGR | Steel Body w/ CL150RF Flanges, 6353 Pilot w/ 3-40 Psig Spring Range,125 Psig Main Spring
51 | 74 | Y | PCV MIX 103 | PCV | MIX | 103 | 9517-PID-105b | Propane-Air to QT Pressure Control Valve | 0.5 | 0.5 | FNPT | Swagelok | KPR1DRC412A20000 | General-Purpose Diaphragm-Sensing, 0-30 psig Range
52 | 82 | Y | PCV MIX 109 | PCV | MIX | 109 | 9517-PID-105c | Air Pressure Control Valve | 2 | 2 | ANSI 150# | Fisher | 1098-EGR | Steel Body w/ CL150RF Flanges, 6353 Pilot w/ 35-125 Psig Spring Range, size 30 actuator
53 | 72 | Y | PCV QT 101 | PCV | QT | 101 | 9517-PID-105b | Pressure Regulator Supply Gas to S.G. Transducer | 0.25 | 0.25 | FNPT | Fisher | R622-BCF | 1/2" NPT, 9" to 13" WC Spring Range
54 | 53 | Y | PE MIX 101 | PE | MIX | 101 | 9517-PID-105b | Static Mixer | 4 | 4 | WELD | Custom | 59571 | CS w/ Sch. 40, A106 Gr B Pipe Housing, OAL = 16" end to end
55 | 58 | Y | PE MIX 102 | PE | MIX | 102 | 9517-PID-105b | Inlet Filter for QT | 0.125 | 0.125 | FNPT | Balston | 91S6 | SS Housing, Coalescing Filter Element
56 | 73 | Y | PE QT 101 | PE | QT | 101 | 9517-PID-105b | Specific Gravity Transducer | 0.375 | 0.25 | Swagelok | Yokogawa | GD402G-A-E-E/U & GD40T/EJAF3 | Specific Gravity Transducer Sample Panel
57 | 22 | Y | PI MIX 102 | PI | MIX | 102 | 9517-PID-105a | Blender Propane Vapor Inlet Pressure Indicator #2 | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
58 | 75 | Y | PI MIX 103 | PI | MIX | 103 | 9517-PID-105b | Blender Air Supply Inlet Pressure Indicator #1 | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
59 | 80 | Y | PI MIX 104 | PI | MIX | 104 | 9517-PID-105c | Blender Air Supply Inlet Pressure Indicator #2 | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
60 | 23 | Y | PI MIX 105 | PI | MIX | 105 | 9517-PID-105a | Blender Propane Vapor Inlet Pressure Indicator #1 | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
61 | 43 | Y | PI MIX 106 | PI | MIX | 106 | 9517-PID-105b | Mixed Gas Pressure Indicator | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
62 | 71 | Y | PI MIX 107 | PI | MIX | 107 | 9517-PID-105b | Propane-Air to QT Pressure Indicator | 0.25 | NA | MNPT | Trerice | D83SS2502LA110 | 2.5" Dial, 0-100 psig, 1/4" LB Mount
63 | 46 | Y | PI MIX 108 | PI | MIX | 108 | 9517-PID-105b | Mixed Gas Pressure Indicator #2 | 0.5 | NA | MNPT | US Gauge | 1981 # 150027DM | 4" Dial, 0-200 Psig Range, 1/2" Lower Mount
64 | 87 | Y | PI QT 101 | PI | QT | 101 | 9517-PID-105c | Pressure Indicator to S.G. Transducer | 0.25 | NA | MNPT | Trerice | 760B2502LT660 | 2.5" Dial, 0-30" WC, 1/4" Lower Mount
65 | 41 | Y | PSH MIX 101 | PSH | MIX | 101 | 9517-PID-105b | Mixed Gas High Pressure Switch | 0.5 | NA | MNPT | Solon | 6PSX-1-2 | Class 1 Div 1 0-300 Scale
66 | 70 | Y | PSV MIX 101 | PSV | MIX | 101 | 9517-PID-105b | QT Inlet Relief Valve | 0.5 | 0.5 | MXFNPT | Fisher | H120-60 | 60 PSIG Set Pressure
67 | 15 | Y | PT MIX 102 | PT | MIX | 102 | 9517-PID-105a | Blender Propane Vapor Pressure Transmitter #2 | 0.5 | NA | MNPT | Wika | E-10 # 50033948 | 0-200 Psig Range, Wire End
68 | 64 | Y | PT MIX 103 | PT | MIX | 103 | 9517-PID-105b | Process Air Inlet Pressure Transmitter #1 | 0.5 | NA | MNPT | Wika | E-10 # 50033948 | 0-200 Psig Range, Wire End
69 | 68 | Y | PT MIX 104 | PT | MIX | 104 | 9517-PID-105b | Blender Air Supply Inlet Pressure Transmitter #2 | 0.5 | NA | MNPT | Wika | E-10 # 50033948 | 0-200 Psig Range, Wire End
70 | 16 | Y | PT MIX 105 | PT | MIX | 105 | 9517-PID-105a | Blender Propane Vapor Pressure Transmitter #1 | 0.5 | NA | MNPT | Wika | E-10 # 50033948 | 0-200 Psig Range, Wire End
71 | 36 | Y | PT MIX 106 | PT | MIX | 106 | 9517-PID-105a | Mixed Gas Pressure Transmitter # 1 | 0.5 | NA | MNPT | Wika | E-10 # 50033948 | 0-200 Psig Range, Wire End
72 | 42 | Y | PT MIX 107 | PT | MIX | 107 | 9517-PID-105b | Mixed Gas Pressure Transmitter # 2 | 0.5 | NA | MNPT | Wika | E-10 # 50033948 | 0-200 Psig Range, Wire End
73 | 14 | Y | RTD MIX 101 | RTD | MIX | 101 | 9517-PID-105a | Blender Propane Vapor Resistance Temperature Device | 0.5 | NA | MNPT | Pyromation | R1T185L483-LS4C2.509-SL-8HN71 | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
74 | 67 | Y | RTD MIX 102 | RTD | MIX | 102 | 9517-PID-105b | Air Resistance Temperature Device | 0.5 | NA | MNPT | Pyromation | R1T185L483-LS4C2.509-SL-8HN71 | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
75 | 34 | Y | RTD MIX 103 | RTD | MIX | 103 | 9517-PID-105a | Mixed Gas Vapor Resistance Temperature Device | 0.5 | NA | MNPT | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
76 | 30 | Y | ST MIX 101 | ST | MIX | 101 | 9517-PID-105a | Blender Propane vapor Inlet Strainer | 2 | 2 | ANSI 150# | Titan | YS-61-CS | Carbon Steel Body, SS 40 Mesh Screen
77 | 90 | Y | ST MIX 102 | ST | MIX | 102 | 9517-PID-105c | Blender Air Inlet Strainer | 2 | 2 | ANSI 150# | Titan | YS-61-CS | Carbon Steel Body, SS 40 Mesh Screen
78 | 13 | Y | TI MIX 101 | TI | MIX | 101 | 9517-PID-105a | Blender Propane Vapor Temperature Indicator | 0.5 | NA | MNPT | Dwyer | BTLR325101 | Bimetal Thermometer, 3" Dial, 0/200 Deg. F, 2.5" Stem
79 | 69 | Y | TI MIX 102 | TI | MIX | 102 | 9517-PID-105b | Blender Air Supply Temperature Indicator | 0.5 | NA | MNPT | Dwyer | BTLS325101 | Bimetal Thermometer, 3" Dial, 0/200 Deg. F, 2.5" Stem
80 | 35 | Y | TI MIX 103 | TI | MIX | 103 | 9517-PID-105a | Mixed Gas Temperature Indicator | 0.5 | NA | MNPT | ReoTemp | AA-040-1-F43/S4C0409 | Bimetal Thermometer, 3" Dial, 0/200 Deg. F, 2.5" Stem
81 | 24 | Y | TW MIX 101 | TW | MIX | 101 | 9517-PID-105a | Blender Propane Vapor Temp. RTD Thermowell | 0.5 | 0.5 | MNPT/FNPT | Pyromation | included with RTD (Part of RTD-MIX-101) | 1/2" Process Connection, 1 7/16" Inserction Length
82 | 25 | Y | TW MIX 102 | TW | MIX | 102 | 9517-PID-105a | Blender Propane Vapor Temp. Indicator Thermowell | 0.5 | 0.5 | MNPT/FNPT | Pyromation | LS4C2.509 (Part of TI-MIX-101) | 1/2" Process Connection, 1 7/16" Inserction Length
83 | 83 | Y | TW MIX 103 | TW | MIX | 103 | 9517-PID-105c | Blender Air Supply Temp. RTD Thermowell | 0.5 | 0.5 | MNPT/FNPT | Pyromation | included with RTD (Part of RTD-MIX-102) | 1/2" Process Connection, 1 7/16" Inserction Length
84 | 81 | Y | TW MIX 104 | TW | MIX | 104 | 9517-PID-105c | Blender Air Supply Temp. Indicator Thermowell | 0.5 | 0.5 | MNPT/FNPT | Pyromation | LS4C2.509 (Part of TI-MIX-102) | 1/2" Process Connection, 2.5" Inserction Length
85 | 40 | Y | TW MIX 105 | TW | MIX | 105 | 9517-PID-105b | Mixed Gas Vapor Temp. RTD Thermowell | 0.5 | 0.5 | MNPT/FNPT | Pyromation | included with RTD (Part of RTD-MIX-103) | 1/2" Process Connection, 2.5" Inserction Length
86 | 39 | Y | TW MIX 106 | TW | MIX | 106 | 9517-PID-105b | Mixed Gas Temperature Indicator Thermowell | 0.5 | 0.5 | MNPT/FNPT | Pyromation | S4C0409 (Part of TI-MIX-103) | 1/2" Process Connection, 2 1/2" Inserction Length
87 | 27 | Y | ZSC MIX 101 | ZSC | MIX | 101 | 9517-PID-105a | Propane Inlet Valve Proof Closed Switch for (FCV-MIX-101) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Closed Limit Switch (Part of FCV-MIX-101)
88 | 88 | Y | ZSC MIX 102 | ZSC | MIX | 102 | 9517-PID-105c | Air Inlet Valve # 1 Proof Closed Switch for (FCV-MIX-104) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Closed Limit Switch (Part of FCV-MIX-104)
89 | 91 | Y | ZSC MIX 103 | ZSC | MIX | 103 | 9517-PID-105c | Air Inlet Valve # 2 Proof Closed Switch for (FCV-MIX-106) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Closed Limit Switch (Part of FCV-MIX-106)
90 | 95 | Y | ZSC MIX 104 | ZSC | MIX | 104 | 9517-PID-105c | Air Vent Proof Closed Switch for (FCV-MIX-108) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Closed Limit Switch (Part of FCV-MIX-108)
91 | 52 | Y | ZSC MIX 105 | ZSC | MIX | 105 | 9517-PID-105b | Proof Closed Switch for (FCV-MIX-121) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Closed Limit Switch (Part of FCV-MIX-121)
92 | 48 | Y | ZSC MIX 106 | ZSC | MIX | 106 | 9517-PID-105b | Tank Vapor Header Proof Closed Switch for (FCV-MIX-123) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Closed Limit Switch (Part of FCV-MIX-108)
93 | 94 | Y | ZSO MIX 102 | ZSO | MIX | 102 | 9517-PID-105c | Air Vent Valve Explosion Proof Open Switch for (FCV-MIX-108) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Open Limit Switch (Part of FCV-MIX-108)
94 | 37 | Y | ZSO MIX 103 | ZSO | MIX | 103 | 9517-PID-105a | Proof Open Switch for (FCV-MIX-123) | 0.5 | NA | NA | StoneL | EN33C02RA | Proof Open Limit Switch (Part of FCV-MIX-123)
?? | 84 | Y | QT 101 |  | QT | 101 | 9517-PID-105c | Not on Device TAG Listing
Note on I32: Bill Franki: Corrected "Porpane"

## 9517-PID-102 (Replaced-Unused)
|  |  |  | PROJECT: |  | Berkshire Gas Co. |  |  |  |  | FILE DATE: | 5/7/2012
|  |  |  | JOB NUMBER: |  | 9517 |  |  |  |  | REVISION DATE: | 7/5/2012
|  |  |  | REF. DRAWING: |  | 9517-PID-102 |  |  |  |  | PRINT DATE: | 1/29/2013 10:56
The information contained in this document and/or electronic file(s) is proprietary and/or confidential property Standby Systems, Inc. and shall not be used, reproduced or disclosed to others without the express written consent of the respective owner(s). If consent for reproduction or disclosure in whole or in part is given, this notice shall be set forth on each document page and/or in each electronic reproduction so authorized.
Entry # | Drawing # | Located Y/N | TAG Search | DEVICE TAG NAME |  |  | REFERENCE DRAWING No. | FUNCTIONAL DESCRIPTION | CONNECT SIZE IN | CONNECT SIZE OUT | CONNECT TYPE | MANUFACTURER NAME | MODEL / CATALOG NUMBER | CONSTRUCTION NOTES
|  |  |  | DEVICE CODE | EQUIP. CODE | ID CODE
1 | 6 | Y | HV AIR 101 | HV | AIR | 101 | 9517-PID-102a | Process Air Compressor Discharge Isolation Valve | 3 | 3 | ANSI 150# | Kuka | CBA15BGLN | Carbon Steel Body, SS Trim, Fire Safe, Full Port
2 | 3 | Y | HV AIR 102 | HV | AIR | 102 | 9517-PID-102a | Process Air Tank Drain Valve | 1 | 1 | FNPT | RUB | S92EB8 | 1" Non-Vented Brass Ball Valve
3 | 4 | Y | HV AIR 103 | HV | AIR | 103 | 9517-PID-102a | Process Air Tank Instrument Isolation Valve | 0.5 | 0.5 | MXFNPT | Dragon | 10M517G | CS Bar Stock Body - 6000 psig Max
4 | 1 | Y | PE AIR 101 | PE | AIR | 101 | 9517-PID-102a | Process Air Compressor | NA | 3 | FNPT | Atlas Copco | GA110-6.9-60 | Oil Injected 150 HP Rotary Screw, 747 SCFM @ 90 psig Capacity
5 | 7 | Y | PE AIR 102 | PE | AIR | 102 | 9517-PID-102a | Process Air Tank | 3 | 3 | ANSI 150# | Sylvin Tank | TBD | 620 Gallon, 3" 150# Flange Connection, ASME
6 | 5 | Y | PI AIR 101 | PI | AIR | 101 | 9517-PID-102a | Process Air Tank Pressure Indicator | 0.5 | 0.5 | MNPT | US Gauge | 1981 # 150027DM | 4.5" Dial, 1/2" Lower Mount, Dry, 0-200 Psig Range
7 | 2 | Y | PSV AIR 101 | PSV | AIR | 101 | 9517-PID-102a | Process Air Tank Relief Valve | 1" | 1/2" | MNPT x FNPT | Kunkle | 6283FEV01 | 978 SCFM Capacity, up to 406 Deg F, 150 Psig Setting
8 | 8 | Y | FCV IAS 106 | FCV | IAS | 106 | 9517-PID-102a | IAS Solenoid Valve for (FCV-VAP-101) | 0.25 | 0.25 | FNPT | Parker Skinner | 71315SN2MNJ1N0H111C2 | 3-way, SS body, 24 VDC, Class F, 10W
9 | 10 | Y | FCV IAS 107 | FCV | IAS | 107 | 9517-PID-102a | IAS Flow Control Valve for (FCV-VAP-101) | 0.125 | 0.125 | FNPT | Schraeder-Bellows | SPF200B | Flow Control Valve 1/8 "
10 | 9 | Y | HV IAS 104 | HV | IAS | 104 | 9517-PID-102a | IAS Vented Ball Valve for (FCV-VAP-101) | 0.25 | 0.25 | FNPT | RUB | S93B41 | 1/4” Brass Ball Valve, Vented
11 | 17 | Y | FCV VAP 101 | FCV | VAP | 101 | 9517-PID-102a | Vaporizer Discharge Actuated Ball Valve | 3 | 3 | ANSI 300# | Kuka/Triac | CBA30BGLN/2R300SR--LT | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim w/ Triac Actuator
12 | 20 | Y | HV VAP 101 | HV | VAP | 101 | 9517-PID-102a | Vaporizer Inlet Isolation Ball Valve | 2 | 2 | ANSI 300# | Kuka | CBA30BGLN | Full Port, Fire Rated, Carbon Steel Body, Stainless Steel Trim
13 | 14 | Y | HV VAP 102 | HV | VAP | 102 | 9517-PID-102a | Instrument Isolation Ball Valve | 0.5 | 0.5 | MNPT x FNPT | Dragon | 10M517G | CS Bar Stock Body - 6000 psig Max
14 | 11 | Y | PA VAP 101 | PA | VAP | 101 | 9517-PID-102a | Vaporizer Relief Stack Cap | 2 | NA | NA | Anthes Weather Cap | WC 5 | Weather Cap
15 | 12 | Y | PA VAP 102 | PA | VAP | 102 | 9517-PID-102a | Vaporizer Relief Valve Pipe Away Adapter | 1.25 | 2 | NPT | Rego | 3135-10 | Relief Valve Pipe Away Adapter
16 | 18 | Y | PE VAP 101 | PE | VAP | 101 | 9517-PID-102a | Q1650V Vertical Waterbath Vaporizer | 1 | 2 | FNPT | Algas-SDI | Q1650V | 1650 GPH Liquid Propane Vaporizer
17 | 15 | Y | PT VAP 101 | PT | VAP | 101 | 9517-PID-102a | Vaporizer Outlet Pressure Transmitter | 0.5 | NA | FNPT | Wika | E-10 # 4365182 | 0-300 Psig Scale, Explosion Proof
18 | 13 | Y | RTD VAP 101 | RTD | VAP | 101 | 9517-PID-102a | Vaporizer Outlet Resistive Temperature Device | 0.5 | NA | FNPT | Pyromation | R1T185L483-S4C0409-SL-8HN71 | 3 Wire, Element, 100 Ohm Platinum, XP Connection Head
19 | 16 | Y | TW VAP 101 | TW | VAP | 101 | 9517-PID-102a | Vaporizer Outlet Thermowell for Temperature Transmitter | 0.5 | NA | FNPT | Pyromation | Part of RTD- VAP-101 | 1/2" Connection, 2.5" Insertion Length
20 | 19 | Y | ST VAP 101 | ST | VAP | 101 | 9517-PID-102a | Vaporizer Inlet Strainer | 2 | 2 | ANSI 300# | Titan | YS-62-CS | Carbon Steel Body, SS 40 Mesh Strainer